## Shutdown December 2025
Sl. No. | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Tag | Study Comments | Proposed Date & Time
1 | OCC_232 | NEEPCO | 132KV/33KV KHANDONG-ICT-1 | D | Element Operation from CCR. | 04/Dec/2025 | 8:00 | 04/Dec/2025 | 16:00 | Existing System Improvement Related Shut Down |  | SD may be availed subject to availability of 132/33kV ICT 2. | 08:00 to 16:00
2 | OCC_232 | NEEPCO | 132KV-KHANDONG-KOPILI -1 | D | To facilitate testing of operation of Switchyard Element Operation from CCR | 04/Dec/2025 | 8:00 | 04/Dec/2025 | 16:00 | Existing System Improvement Related Shut Down |  | SD may be availed subject to availability of 132kV Khandong-Kopili 2, Khandong Khleiriat link and khandong-Umrangshu-Haflong link. | 08:00 to 16:00
3 | OCC_232 | NEEPCO | 132KV-KHANDONG-KHLIEHRIAT-2 | D | To facilitate testing of operation of Switchyard Element Operation from CCR | 05/Dec/2025 | 8:00 | 05/Dec/2025 | 16:00 | Existing System Improvement Related Shut Down |  | SD may be availed subject to availability of 132KV-KHANDONG-KHLIEHRIAT-1, 132kV Khandong-Kopili-Haflong(PG) link, khandong-Kopili link | 05-12-2025 08:00 to 16:00
4 | OCC_232 | NEEPCO | 132KV-KHANDONG-UMRANSHU-1 | D | To facilitate testing of operation of Switchyard Element Operation from CCR | 04/Dec/2025 | 8:00 | 04/Dec/2025 | 16:00 | Existing System Improvement Related Shut Down |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link | 08:00 to 16:00
5 | OCC_232 | NEEPCO | KHANDONG - UNIT 2 | C | Switchyard Operation from CCR. *Water leakage from Shaft Seal to be attended. *RTD replacement in LCB Thrust pad . *Installation of Emergency Push Button Switch. *Replacement of "O" Ring & Oil leakage to be addressed from LCB. | 04/Dec/2025 | 09:00 | 05/Dec/2025 | 23:59 | Existing System Normal Maintenance Related Shut Down |  | SD may be availed. Consent of beneficiary is required.
6 | OCC_232 | NEEPCO | KHANDONG - UNIT 1 | C | Replacement of MIV Maintanance Seal. *Replacement of Thrust Pad RTD. *Installation of Emergency Push Button Switch, Integration, Program loading etc. *Switchyard Operation from CCR. | 01/Dec/2025 | 09:00 | 04/Dec/2025 | 23:59 | Existing System Normal Maintenance Related Shut Down |  | SD may be availed. Consent of beneficiary is required.
7 | OCC_232 | NTPC | BGTPP - 400KV - BUS 2 | D | For PM 4-989B Isolator PM | 17/Dec/2025 | 7:00 | 17/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed. All elements to be transferred to other bus before SD | 17-12-2025 07:00 to 16:00
8 | OCC_232 | NTPC | BGTPP - 400KV - BUS 1 | D | For PM 4-989A Isolator PM | 16/Dec/2025 | 7:00 | 16/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed. All elements to be transferred to other bus before SD | 16-12-2025 07:00 to 16:00
9 | OCC_232 | NTPC | BUS COUPLER BAY () OF BGTPP - 400KV - BUS 1 AND BGTPP - 400KV - BUS 2 @BGTPP - 400KV | D | For PM 4-989A and B Isolator | 17/Dec/2025 | 7:00 | 17/Dec/2025 | 16:00 |  |  | SD may be availed | 17-12-2025 07:00 to 16:00
10 | OCC_232 | NTPC | 220 KV,315 MVA ICT 2 BAY AT BGTPP | C | PM of ICT-2 220KV bay breaker | 16/Dec/2025 | 7:00 | 18/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of ICT 1 at BGTPP NTPC. 400kV BGTPP-Bongaigaon(PG) DC line, 400/220 KV ICT 1 and 2 at Bongaiagon(PG) and 220kV Bongaigaon(PG)-Salakati-BTPS DC link needs to be present. Combined loading of 220kV Salakati-BTPS D/C needs to be maintained under 430 MW. SPS related to overloading of 220 kV BTPS - Salakati D/C Line to be kept ON. Consent from Assam | 16-12-2025 till 18-12-2025 07:00 to 16:00
11 | OCC_232 | NTPC | 400 KV,315 MVA ICT 2 BAY AT BGTPP | C | PM of ICT-2 400KV bay breaker | 16/Dec/2025 | 7:00 | 18/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of ICT 1 at BGTPP NTPC. 400kV BGTPP-Bongaigaon(PG) DC line, 400/220 KV ICT 1 and 2 at Bongaiagon(PG) and 220kV Bongaigaon(PG)-Salakati-BTPS DC link needs to be present. Combined loading of 220kV Salakati-BTPS D/C needs to be maintained under 430 MW. SPS related to overloading of 220 kV BTPS - Salakati D/C Line to be kept ON. Consent from Assam | 16-12-2025 till 18-12-2025 07:00 to 16:00
12 | OCC_232 | NTPC | BUS COUPLER BAY () OF BGTPP - 400KV - BUS 1 AND BGTPP - 400KV - BUS 2 @BGTPP - 400KV | D | For PM 4-989A and B Isolator | 16/Dec/2025 | 7:00 | 16/Dec/2025 | 16:00 |  |  | SD may be availed | 16-12-2025 07:00 to 16:00
13 | OCC_232 | NTPC | 400KV/220KV BGTPP-ICT-2 | C | ICT-2 PM Activities | 16/Dec/2025 | 7:00 | 18/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of ICT 1 at BGTPP NTPC. 400kV BGTPP-Bongaigaon(PG) DC line, 400/220 KV ICT 1 and 2 at Bongaiagon(PG) and 220kV Bongaigaon(PG)-Salakati-BTPS DC link needs to be present. Combined loading of 220kV Salakati-BTPS D/C needs to be maintained under 430 MW. SPS related to overloading of 220 kV BTPS - Salakati D/C Line to be kept ON. Consent from Assam | 16-12-2025 till 18-12-2025 07:00 to 16:00
14 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
15 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
16 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
17 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
18 | OCC_232 | POWERGRID | 220 KV, 315 MVA ICT 2 BAY AT MISA | C | CB Mechanism Overhauling works | 08/Dec/2025 | 8:00 | 11/Dec/2025 | 16:00 | ICT#2 shall remain charged . | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of no outage of other element. ICT 2 will be remain connected. | 08:00 to 16:00
19 | OCC_232 | POWERGRID | 400 KV, 80 MVAR BUS REACTOR 3 BAY AT BONGAIGAON | C | CB Mechanism Overhauling works | 29/Dec/2025 | 8:00 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, Bus reactor 3 and 4 at Bongaiagon share the same bay. Shares the dia with BTPS ckt 2 | 08:00 to 16:00
20 | OCC_232 | POWERGRID | 400KV-AZARA-SILCHAR L/R@ SILCHAR - 400KV | D | AMP WORKS | 08/Dec/2025 | 8:00 | 08/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed | 08:00 to 16:00
21 | OCC_232 | POWERGRID | FILTER BANK 3 SUB BANK 5 at BNC | D | AMP Works | 06/Dec/2025 | 8:00 | 06/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required | 08:00 to 16:00
22 | OCC_232 | POWERGRID | FILTER BANK 3 SUB BANK 4 at BNC | D | AMP Works | 05/Dec/2025 | 8:00 | 05/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required | 08:00 to 16:00
23 | OCC_232 | POWERGRID | FILTER BANK 3 SUB BANK 3 at BNC | D | AMP Works | 04/Dec/2025 | 8:00 | 04/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required | 08:00 to 16:00
24 | OCC_232 | POWERGRID | 400KV/220KV MISA-ICT-3 | D | Replacement of Electomechanical relay with Numerical Relay for LV OC /EF in ICT-3 with same settings at MISA Ss | 17/Dec/2025 | 08:00 | 17/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | SD may be availed subject to the availability of 400/220 kV ICT 1 and ICT 2 | 08:00 to 16:00
25 | OCC_232 | POWERGRID | 132KV/33KV NAMSAI-ICT-2 | D | 1. PRV microswitch replacement works 2. Capacitance & Tan-Delta Measurement of Bushing & CT 3. H. 4. Aircel Charging Works in B-phase unit. | 16/Dec/2025 | 07:00 | 16/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. Consent from AP is required. | 07:00 to 16:00
26 | OCC_232 | POWERGRID | 220KV/132KV DIMAPUR (PG)-ICT-3 | D | Upgradation of NIFPS System | 15/Dec/2025 | 08:00 | 15/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | SD may be availed subject to the availability of 220kV ICT 1 and 2 at Dimapur | 08:00 to 16:00
27 | OCC_232 | POWERGRID | 220KV/132KV SALAKATI-ICT-3 | D | Upgradation of NIFPS System | 13/Dec/2025 | 07:00 | 13/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | SD may be availed subject to the availability of other ICTs | 07:00 to 16:00
28 | OCC_232 | POWERGRID | 220KV/132KV SALAKATI-ICT-2 | D | Upgradation of NIFPS System | 12/Dec/2025 | 07:00 | 12/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | SD may be availed subject to the availability of other ICTs | 07:00 to 16:00
29 | OCC_232 | POWERGRID | 220KV/132KV SALAKATI-ICT-1 | D | Upgradation of NIFPS System | 11/Dec/2025 | 07:00 | 11/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | SD may be availed subject to the availability of other ICTs | 07:00 to 16:00
30 | OCC_232 | POWERGRID | 132KV/33KV NAMSAI-ICT-1 | D | 1. PRV microswitch replacement works 2. Capacitance & Tan-Delta Measurement of Bushing & CT 3. | 09/Dec/2025 | 07:00 | 09/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. Consent from AP is required. | 07:00 to 16:00
31 | OCC_232 | POWERGRID | 400KV/132KV SILCHAR-ICT-3 | D | AMP WORKS | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 400/132kV Ict 1 and 2 | 08:00 to 16:00
32 | OCC_232 | POWERGRID | 132KV/33KV TEZU-ICT-2 | D | AMP WORKS | 04/Dec/2025 | 07:00 | 04/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. Consent from AP is required. | 07:00 to 16:00
33 | OCC_232 | POWERGRID | 132KV/33KV ROING-ICT-1 | C | OVERHAULING OF 02 NOS CB POLE. REPLACEMENT OF PRD LIMIT SWITCH IN ICT. AMP OF ICT AND BAY EQUIPMENS. | 03/Dec/2025 | 08:00 | 04/Dec/2025 | 16:00 | DURING NIGHT TIME O NON WORKING OF CRANE AT SITE ICT SHALL BE CHARGED THROUGH TBC BAY. | R&U works Related Shut Down under PSDF | SD may be availed. Consent from AP is required. | 08:00 to 16:00
34 | OCC_232 | POWERGRID | 132KV/33KV TEZU-ICT-1 | D | AMP WORKS | 02/Dec/2025 | 07:00 | 02/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. Consent from AP is required. | 07:00 to 16:00
35 | OCC_232 | POWERGRID | BALIPARA - 400KV - BUS 2 | D | AMP WORKS | 29/Dec/2025 | 08:00 | 29/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of Balipara Bus 1 and all the elements must be charged though tie. Bus protection must be in ON condition | 08:00 to 16:00
36 | OCC_232 | POWERGRID | BALIPARA - 400KV - BUS 1 | D | AMP WORKS | 24/Dec/2025 | 08:00 | 24/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of Balipara Bus 2 and all the elements must be charged though tie. Bus protection must be in ON condition | 08:00 to 16:00
37 | OCC_232 | POWERGRID | 400 KV, 80 MVAR BUS REACTOR 3 BAY AT BONGAIGAON | C | CB Mechanism Overhauling works | 29/Dec/2025 | 08:00 | 31/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, Bus reactor 3 and 4 at Bongaiagon share the same bay. Shares the dia with BTPS ckt 2 | 08:00 to 16:00
38 | OCC_232 | POWERGRID | BTPS(NTPC) II (FUTURE) & 2X 80 MVAR BUS REACTOR III AND IVAT BONGAIGAON | C | CB Mechnaism overhauling | 26/Dec/2025 | 08:00 | 28/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of NTPC- Bongaigaon ckt 2 and Ckt 1 must be charged though main bay | 08:00 to 16:00
39 | OCC_232 | POWERGRID | MAIN BAY () OF BALIPARA - 400KV B/R 1 @BALIPARA - 400KV | D | AMP WORKS | 22/Dec/2025 | 08:00 | 22/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, 400kV BR 1 shares dia with 315 mVA ICT 1 at Balipara. Under N-1 of ICT 1 Misa-Samaguri D/C, Kameng khupi-Bailipara link must be in service. | 08:00 to 16:00
40 | OCC_232 | POWERGRID | 400 KV BGTPP 2 BAY AT BONGAIGAON | C | CB Mechanism Overhauling works | 22/Dec/2025 | 08:00 | 25/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, dia must be in service | 08:00 to 16:00
41 | OCC_232 | POWERGRID | MAIN (2) BAY OF 400KV-BALIPARA-MISA-1 @MISA - 400KV | D | AMP Works | 19/Dec/2025 | 08:00 | 19/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to Misa-Balipara 2 and Balipara-Misa to be charged through Tie bay | 08:00 to 16:00
42 | OCC_232 | POWERGRID | TIE BAY () OF BALIPARA - 400KV B/R 3 AND FUTURE @BALIPARA - 400KV | D | AMP WORKS | 19/Dec/2025 | 08:00 | 19/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be subject to no outage elements | 08:00 to 16:00
43 | OCC_232 | POWERGRID | 400 KV BGTPP 1 BAY AT BONGAIGAON | C | CB Mechanism Overhauling works | 18/Dec/2025 | 08:00 | 21/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, dia must be in service | 08:00 to 16:00
44 | OCC_232 | POWERGRID | 132 KV, 50 MVA ICT 2 BAY AT SALAKATI | D | AMP works , FOR BAY AMP WORK. | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 16:00 | (DURING THE SHUTDOWN PERIOD 50MVA ICT-2 WILL BE CHARGED THROUGH TO TBC BAY) | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of other ICTs | 08:00 to 16:00
45 | OCC_232 | POWERGRID | 220 KV, 50 MVA ICT 2 BAY AT SALAKATI | D | AMP works , FOR BAY AMP WORK. | 15/Dec/2025 | 08:00 | 15/Dec/2025 | 16:00 | (DURING THE SHUTDOWN PERIOD 50MVA ICT-2 WILL BE CHARGED THROUGH TO TBC BAY) | R&U works Related Shut Down under PSDF | SD may be subject to the availability other ICTs | 08:00 to 16:00
46 | OCC_232 | POWERGRID | TIE BAY (414) OF 400KV-BALIPARA-BONGAIGAON-1 AND 400KV-BONGAIGAON-ALIPURDUAR-1 @BONGAIGAON - 400KV | D | AMP WORKS | 13/Dec/2025 | 08:00 | 13/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to no outage of elements | 08:00 to 16:00
47 | OCC_232 | POWERGRID | MAIN BAY (02) OF 400KV/220KV MISA-ICT-2 @MISA - 400KV | C | CB Mechnaism overhauling , | 12/Dec/2025 | 20:03 | 16/Dec/2025 | 20:03 | ICT#2 shall remain charged . | R&U works Related Shut Down under PSDF | SD may be availed subect to availability of ICT 1 and 3 at Misa.
48 | OCC_232 | POWERGRID | MAIN BAY () OF 400KV-BISWANATH CHARIALI-SUBANSIRI-2 @BISWANATH CHARIALI - 400KV | D | AMP Works | 12/Dec/2025 | 08:00 | 12/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed | 08:00 to 16:00
49 | OCC_232 | POWERGRID | MAIN BAY () OF MARIANI (PG) - 400KV B/R 2 @MARIANI (PG) - 400KV | D | AMP Works | 12/Dec/2025 | 08:00 | 12/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | Sd may be availed
50 | OCC_232 | POWERGRID | MAIN BAY (2) OF 400KV/132KV BISWANATH CHARIALI-ICT-1 @BISWANATH CHARIALI - 132KV | D | AMP WORKS | 11/Dec/2025 | 08:00 | 11/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subjecte to the availability of 400/132kV ICT 2 at BNCRanganadi-pare-nirjuli-Gohpur-BNC link, Ranaganadi-Lekhi-Nirjuli-Gohpur link. 400kV ICT 1 and ICT2 tie bay at BNC must be in service | 08:00 to 16:00
51 | OCC_232 | POWERGRID | 132 KV, 50 MVA ICT 1 BAY AT SALAKATI | D | AMP works , FOR BAY AMP WORK. | 10/Dec/2025 | 08:00 | 10/Dec/2025 | 16:00 | (DURING THE SHUTDOWN PERIOD 50MVA ICT-1 WILL BE CHARGED THROUGH TO TBC BAY) | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of other ICTs | 08:00 to 16:00
52 | OCC_232 | POWERGRID | MAIN BAY () OF 400KV/220KV MARIANI (PG)-ICT-1 @MARIANI (PG) - 400KV(406) | D | AMP Works | 10/Dec/2025 | 08:00 | 10/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may availed subject to no outage of elements. Shares dia with Misa 2
53 | OCC_232 | POWERGRID | 220 KV, 50 MVA ICT 1 BAY AT SALAKATI | D | AMP works , FOR BAY AMP WORK. | 09/Dec/2025 | 08:00 | 09/Dec/2025 | 16:00 | (DURING THE SHUTDOWN PERIOD 50MVA ICT-1 WILL BE CHARGED THROUGH TO TBC BAY) | R&U works Related Shut Down under PSDF | SD may be subject to the availability other ICTs | 08:00 to 16:00
54 | OCC_232 | POWERGRID | 400 KV BALIPARA 1 BAY AT HVDC BNC | D | AMP WORKS | 09/Dec/2025 | 08:00 | 09/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, 400kV Balipara 1 shares dia with Ranganadi 1 | 08:00 to 16:00
55 | OCC_232 | POWERGRID | 220 KV, 315 MVA ICT 2 BAY AT MISA | C | CB Mechanism Overhauling works | 08/Dec/2025 | 08:00 | 11/Dec/2025 | 16:00 | ICT#2 shall remain charged . | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of no outage of other element. ICT 2 will be remain connected. | 08:00 to 16:00
56 | OCC_232 | POWERGRID | 400 KV BISWANATH CHARIALI 3 MAIN BAY (415) AT BALIPARA | C | CB MECHNAISM OVERHAULING WORKS | 08/Dec/2025 | 08:00 | 11/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed, BNC 3 shares dia with Bongaigaon 1 | 08:00 to 16:00
57 | OCC_232 | POWERGRID | FILTER BANK1 MAIN BAY AT BNC | D | AMP WORKS | 08/Dec/2025 | 08:00 | 08/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required | 08:00 to 16:00
58 | OCC_232 | POWERGRID | BUS SECTIONALIZER BAY () OF BISWANATH CHARIALI - 400KV - BUS 3(2A) AND BISWANATH CHARIALI - 400KV - BUS 4(2B) @BISWANATH CHARIALI - 400KV | D | AMP Works | 03/Dec/2025 | 08:00 | 03/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | Sd may be availed subject to no outage of elements | 08:00 to 16:00
59 | OCC_232 | POWERGRID | 400 KV BONGAIGAON 3 MAIN BAY(WITH 63 MVAR LINE REACTOR ) (419) AT BALIPARA | C | CB Mechanism Overhauling works | 03/Dec/2025 | 08:00 | 06/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subjkect to availability of 400kV Balipara-Bongaigaon 1,2 and 4 | 08:00 to 16:00
60 | OCC_232 | POWERGRID | BUS SECTIONALIZER BAY () OF BISWANATH CHARIALI - 400KV - BUS 1(1A) AND BISWANATH CHARIALI - 400KV - BUS 2(1B) @BISWANATH CHARIALI - 400KV | D | AMP Works | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | Sd may be availed subject to no outage of elements | 08:00 to 16:00
61 | OCC_232 | POWERGRID | MAIN (1) BAY OF 400KV/220KV MISA-ICT-2 @MISA - 400KV | C | CB Mechnaism overhauling , | 01/Dec/2025 | 08:00 | 05/Dec/2025 | 16:00 | ICT#2 shall remain charged . | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of ICT 1 and 3 at Misa | 08:00 to 16:00
62 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
63 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 31/Dec/2025 | 7:30 | 31/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
64 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 30/Dec/2025 | 7:30 | 30/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
65 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 30/Dec/2025 | 7:30 | 30/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
66 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 29/Dec/2025 | 7:30 | 29/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
67 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 29/Dec/2025 | 7:30 | 29/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
68 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 28/Dec/2025 | 7:30 | 28/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
69 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 28/Dec/2025 | 7:30 | 28/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
70 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 27/Dec/2025 | 7:30 | 27/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
71 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 27/Dec/2025 | 7:30 | 27/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
72 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 26/Dec/2025 | 7:30 | 26/Dec/2025 | 16:00 |  |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. | 07:30 to 16:00
73 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (AS)-1 | D | AR in Non-auto mode for replacment of insulator in other ckt | 26/Dec/2025 | 7:30 | 26/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
74 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 25/Dec/2025 | 7:30 | 25/Dec/2025 | 16:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
75 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 25/Dec/2025 | 7:30 | 25/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
76 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 25/Dec/2025 | 7:30 | 25/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. FTC procedure to be followed | 07:00 to 16:00
77 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 24/Dec/2025 | 7:30 | 24/Dec/2025 | 16:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
78 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 24/Dec/2025 | 7:30 | 24/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
79 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 31/Dec/2025 | 7:00 | 31/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 31-12-2025 07:00 to 16:00
80 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 24/Dec/2025 | 7:00 | 24/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
81 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 23/Dec/2025 | 09:00 | 23/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
82 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 23/Dec/2025 | 09:00 | 23/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
83 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 23/Dec/2025 | 7:30 | 23/Dec/2025 | 16:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
84 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 23/Dec/2025 | 7:30 | 23/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
85 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 30/Dec/2025 | 7:00 | 30/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 30-12-2025 07:00 to 16:00
86 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 23/Dec/2025 | 7:00 | 23/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
87 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 22/Dec/2025 | 09:00 | 22/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
88 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 22/Dec/2025 | 09:00 | 22/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
89 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 22/Dec/2025 | 08:30 | 22/Dec/2025 | 17:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
90 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 22/Dec/2025 | 08:30 | 22/Dec/2025 | 17:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
91 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 29/Dec/2025 | 7:00 | 29/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 29-12-2025 07:00 to 16:00
92 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 22/Dec/2025 | 7:00 | 22/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
93 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 21/Dec/2025 | 09:00 | 21/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
94 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 21/Dec/2025 | 09:00 | 21/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
95 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 21/Dec/2025 | 7:30 | 21/Dec/2025 | 16:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
96 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 21/Dec/2025 | 7:30 | 21/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
97 | OCC_232 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 21/Dec/2025 | 08:00 | 21/Dec/2025 | 17:00 |  |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh | 07:00 to 16:00
98 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 28/Dec/2025 | 7:00 | 28/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 28-12-2025 07:00 to 16:00
99 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 21/Dec/2025 | 7:00 | 21/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
100 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 20/Dec/2025 | 09:00 | 20/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
101 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 20/Dec/2025 | 09:00 | 20/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
102 | OCC_232 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Mariani TLM . | 20/Dec/2025 | 7:30 | 20/Dec/2025 | 16:00 |  |  | SD may be availed. SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(PG) line.Under N-1 condition, Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 245 MW (during non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link. | 07:30 to 16:00
103 | OCC_232 | POWERGRID | A/R of 220KV-AGBPP-MARIANI (PG) | D | AR in Non-auto mode for replacment of insulator in other ckt | 20/Dec/2025 | 7:30 | 20/Dec/2025 | 16:00 |  |  | SD may be availed. A/R may be kept in non auto mode | 07:30 to 16:00
104 | OCC_232 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 20/Dec/2025 | 7:00 | 20/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh | 07:00 to 16:00
105 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 27/Dec/2025 | 7:00 | 27/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 27-12-2025 07:00 to 16:00
106 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 20/Dec/2025 | 7:00 | 20/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
107 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 19/Dec/2025 | 09:00 | 19/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
108 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 19/Dec/2025 | 09:00 | 19/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
109 | OCC_232 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | 220 kV Balipara-Sonabil 1 Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 19/Dec/2025 | 8:00 | 19/Dec/2025 | 16:00 |  |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | 08:00 to 16:00
110 | OCC_232 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 19/Dec/2025 | 7:00 | 19/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh | 07:00 to 16:00
111 | OCC_232 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | Installation of TLA in Transmisision line | 26/Dec/2025 | 7:00 | 26/Dec/2025 | 16:00 |  |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. | 26-12-2025 07:00 to 16:00
112 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 19/Dec/2025 | 7:00 | 19/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
113 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 18/Dec/2025 | 09:00 | 18/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
114 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 18/Dec/2025 | 09:00 | 18/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
115 | OCC_232 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | 220 kV Balipara-Sonabil 1 Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 18/Dec/2025 | 8:00 | 18/Dec/2025 | 16:00 |  |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | 08:00 to 16:00
116 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 18/Dec/2025 | 7:00 | 18/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
117 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/Dec/2025 | 09:00 | 17/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
118 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 17/Dec/2025 | 09:00 | 17/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
119 | OCC_232 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | 220 kV Balipara-Sonabil 2 Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 17/Dec/2025 | 8:00 | 17/Dec/2025 | 16:00 |  |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | 08:00 to 16:00
120 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | D | Installation of TLA in Transmisision line | 17/Dec/2025 | 7:00 | 17/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
121 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 17/Dec/2025 | 7:00 | 17/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
122 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/Dec/2025 | 09:00 | 16/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
123 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 16/Dec/2025 | 09:00 | 16/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
124 | OCC_232 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | 220 kV Balipara-Sonabil 2 Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 16/Dec/2025 | 8:00 | 16/Dec/2025 | 16:00 |  |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | 08:00 to 16:00
125 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | D | Installation of TLA in Transmisision line | 16/Dec/2025 | 7:00 | 16/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-1 | 07:00 to 16:00
126 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 16/Dec/2025 | 7:00 | 16/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
127 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 15/Dec/2025 | 09:00 | 15/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
128 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 15/Dec/2025 | 09:00 | 15/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
129 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | D | Installation of TLA in Transmisision line | 15/Dec/2025 | 7:00 | 15/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-1 | 07:00 to 16:00
130 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 15/Dec/2025 | 7:00 | 15/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
131 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 14/Dec/2025 | 09:00 | 14/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
132 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 14/Dec/2025 | 09:00 | 14/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
133 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | D | Installation of TLA in Transmisision line | 14/Dec/2025 | 7:00 | 14/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-1 | 07:00 to 16:00
134 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 14/Dec/2025 | 7:00 | 14/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
135 | OCC_232 | POWERGRID | 132KV-BALIPARA-KHUPI-1 | D | AMP Works | 13/Dec/2025 | 8:00 | 13/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of kameng-Khupi link. Consent from AP | 08:00 to 16:00
136 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/Dec/2025 | 09:00 | 13/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
137 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 13/Dec/2025 | 09:00 | 13/Dec/2025 | 16:30 |  |  | SD may be availed.A/R may be kept in non auto mode
138 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | D | Installation of TLA in Transmisision line | 13/Dec/2025 | 7:00 | 13/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-1 | 07:00 to 16:00
139 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 13/Dec/2025 | 7:00 | 13/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
140 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 12/Dec/2025 | 09:00 | 12/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
141 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 12/Dec/2025 | 09:00 | 12/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
142 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | Installation of TLA in Transmisision line | 12/Dec/2025 | 7:00 | 12/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
143 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 12/Dec/2025 | 7:00 | 12/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
144 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
145 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
146 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | Installation of TLA in Transmisision line | 11/Dec/2025 | 7:00 | 11/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
147 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 11/Dec/2025 | 7:00 | 11/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
148 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
149 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 2, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
150 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | Installation of TLA in Transmisision line | 10/Dec/2025 | 7:00 | 10/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
151 | OCC_232 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | Installation of TLA in Transmisision line | 10/Dec/2025 | 7:00 | 10/Dec/2025 | 16:00 |  |  | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present. | 07:00 to 16:00
152 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
153 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
154 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | Installation of TLA in Transmisision line | 09/Dec/2025 | 7:00 | 09/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
155 | OCC_232 | POWERGRID | 132KV-TEZU-NAMSAI-1 | C | Permanent restoration of vulnerable loc 75, 76 132kV Tezu-Namsai due to soil erosion by River Lohit (ERS at present). 2 nos. new tower erection. | 08/Dec/2025 | 8:00 | 17/Dec/2025 | 16:00 |  | Contruction | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required. FTC procedure to be followed | 08:00 to 16:00
156 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
157 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-1 | D | AR in Non-autpo mode for replacment of insulator in ckt#2. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
158 | OCC_232 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | Installation of TLA in Transmisision line | 08/Dec/2025 | 7:00 | 08/Dec/2025 | 16:00 |  |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2. | 07:00 to 16:00
159 | OCC_232 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-1 | C | FOR SHIFTING FROM VULNERABLE TOWER NO 305 AND 458 TO NEW PILE FOUNDATION TOWERS ON ACCOUNT OF CHNAGES IN THE RIVER COURSE(River Nonai & River Mora Pagladia ) | 07/Dec/2025 | 8:00 | 22/Dec/2025 | 16:00 |  | Contruction | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 3 and 4, 400kV Bongaigaon-Mirza and 400kV Bongaiagon-Killing. FTC procedure to be followed | 08:00 to 16:00
160 | OCC_232 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-2 | C | FOR SHIFTING FROM VULNERABLE TOWER NO 305 AND 458 TO NEW PILE FOUNDATION TOWERS ON ACCOUNT OF CHNAGES IN THE RIVER COURSE(River Nonai & River Mora Pagladia ) | 07/Dec/2025 | 8:00 | 22/Dec/2025 | 16:00 |  | Contruction | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 3 and 4, 400kV Bongaigaon-Mirza and 400kV Bongaiagon-Killing. FTC procedure to be followed | 08:00 to 16:00
161 | OCC_232 | POWERGRID | 132KV-RANGIA-MOTONGA-1 | D | AMP Works , CT testing works | 06/Dec/2025 | 8:00 | 06/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed. NLDC /Bhutan consent is required. Consent from Assam | 08:00 to 16:00
162 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 06/Dec/2025 | 09:00 | 06/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
163 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-2 | D | AR in Non-autpo mode for replacment of insulator in ckt#1. | 06/Dec/2025 | 09:00 | 06/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
164 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 05/Dec/2025 | 09:00 | 05/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
165 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-2 | D | AR in Non-autpo mode for replacment of insulator in ckt#1. | 05/Dec/2025 | 09:00 | 05/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
166 | OCC_232 | POWERGRID | 132KV-SILCHAR-HAILAKANDI-1 | D | AMP WORKS | 05/Dec/2025 | 7:00 | 05/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132 kV Hailakandi(Assam)-Silchar-Hailakandi ckt 2 and Panchgram-Hailakandi link. Consent from Assam | 07:00 to 16:00
167 | OCC_232 | POWERGRID | 220KV-SALAKATI-BTPS-2 | D | AMP Works | 04/Dec/2025 | 8:00 | 04/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 400/220kV ICT 1 and 2 BGTPP, 400kV Bongaigaon-Mirza, 200kV Salakati-BTPS 1. SPS related to overloading of Salakati-BTPS needs to be in ON condition. Consent from Assam | 08:00 to 16:00
168 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
169 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-2 | D | AR in Non-autpo mode for replacment of insulator in ckt#1. | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
170 | OCC_232 | POWERGRID | 132KV-AGTCCPP-KUMARGHAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 03/Dec/2025 | 7:00 | 03/Dec/2025 | 16:00 |  | Existing System Improvement Related Shut Down | Sd may be availed subject to the availability of Badarpur-karimganj-Kumarghat link and PK Bari-Kumarghat. Intimation to NEEPCO | 07:00 to 16:00
171 | OCC_232 | POWERGRID | 220KV-SALAKATI-BTPS-1 | D | AMP Works | 03/Dec/2025 | 8:00 | 03/Dec/2025 | 16:00 |  | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 400/220kV ICT 1 and 2 BGTPP, 400kV Bongaigaon-Mirza, 200kV Salakati-BTPS 2. SPS related to overloading of Salakati-BTPS needs to be in ON condition. Consent from Assam | 08:00 to 16:00
172 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 03/Dec/2025 | 09:00 | 03/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
173 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-2 | D | AR in Non-autpo mode for replacment of insulator in ckt#1. | 03/Dec/2025 | 09:00 | 03/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
174 | OCC_232 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 02/Dec/2025 | 09:00 | 02/Dec/2025 | 16:30 |  |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link, 220kV Misa-Samaguri link
175 | OCC_232 | POWERGRID | A/R of 400KV-MISA-MARIANI (PG)-2 | D | AR in Non-autpo mode for replacment of insulator in ckt#1. | 02/Dec/2025 | 09:00 | 02/Dec/2025 | 16:30 |  |  | SD may be availed. A/R may be kept in non auto mode
176 | OCC_232 | AEGCL | AZARA - 400KV B/R 1 | D | ROUTINE TESTING OF EQUIPMENT | 23/Dec/2025 | 08:00 | 23/Dec/2025 | 16:00 | AGM MIRZA | Existing System Normal Maintenance Related Shut Down | SD may be availed
177 | OCC_232 | AEGCL | 220KV/132KV MARIANI (AS)-ICT-2 | C | REPLACEMENT OF AIRCELLS, BUTTERFLY VALVES AND ARRESTING OF OIL LEAKAGE | 16/Dec/2025 | 08:00 | 25/Dec/2025 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 220/132 KV ICT 1 at Mariani, Dimapur-Bokajan-Sarupathar-Golaghat-mariani link, Kathalguri-Tinsukia-Ntps-Lakwa-Nazira-Teok-Jorhat link. Sensitivity of ICTs are 55% wrt each other.
178 | OCC_232 | AEGCL | 400KV/220KV AZARA-ICT-2 | D | ROUTINE TESTING | 09/Dec/2025 | 08:00 | 09/Dec/2025 | 16:00 | AGM MIRZA | R&U works Related Shut Down under PSDF | SD may be availed sibject to availability of 400/220kV ICT 1 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link
179 | OCC_232 | AEGCL | 220KV/132KV MARIANI (AS)-ICT-1 | C | REPLACEMENT OF AIRCELLS, BUTTERFLY VALVES AND ARRESTING OF OIL LEAKAGE | 06/Dec/2025 | 08:00 | 15/Dec/2025 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 220/132 KV ICT 2 at Mariani, Dimapur-Bokajan-Sarupathar-Golaghat-mariani link, Kathalguri-Tinsukia-Ntps-Lakwa-Nazira-Teok-Jorhat link. Sensitivity of ICTs are 55% wrt each other.
180 | OCC_232 | AEGCL | 400KV/220KV AZARA-ICT-1 | D | ROUTINE TESTING | 05/Dec/2025 | 08:00 | 05/Dec/2025 | 16:00 | AGM MIRZA | R&U works Related Shut Down under PSDF | SD may be availed sibject to availability of 400/220kV ICT 2 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link
181 | OCC_232 | AEGCL | SRIKONA - 132KV - BUS 1 | D | MAIN BUS, PREVENTIVE MAINTENANCE | 21/Dec/2025 | 05:00 | 21/Dec/2025 | 12:00 | AGM SILCHAR T&T | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of Badarpur- Panchgram-Hailakandi-silchar link, Jiribam-Pailapool link
182 | OCC_232 | AEGCL | DULLAVCHERRA - 132KV - BUS 1 | D | MAIN BUS, 132kV RAILWAY BAY CONSTRUCTION WORK | 14/Dec/2025 | 06:00 | 14/Dec/2025 | 10:00 | AGM PANHGRAM ( THERE IS ONLY ONE BUS) | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132kV PK Bari-Dharmanagar. Consent from Tripura
183 | OCC_232 | AEGCL | RUPAI - 132KV - BUS 1 | D | MAIN BUS, PREVENTIVE MAINTENANCE | 05/Dec/2025 | 05:30 | 05/Dec/2025 | 08:30 | RE RUPAI( THERE IS ONLY ONE BUS) | R&U works Related Shut Down under PSDF | Sd may be availed subject to the availability of Kathalguri-Namsai-Tezu-Roing link and Ranaganadi-Ziro-basar-Pasighat-Roing -Chapakhowa link. Consent of AP is required.
184 | OCC_232 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 30/Dec/2025 | 09:00 | 30/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
185 | OCC_232 | AEGCL | 220KV-AGIA-AZARA-1 | D | CORRIDOR CLEANING | 29/Dec/2025 | 08:30 | 29/Dec/2025 | 16:30 | AGM T&T GOALPARA & AGM SSJI | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
186 | OCC_232 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 26/Dec/2025 | 08:00 | 26/Dec/2025 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
187 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 25/Dec/2025 | 08:00 | 25/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
188 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 24/Dec/2025 | 08:00 | 24/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
189 | OCC_232 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING | 23/Dec/2025 | 10:00 | 23/Dec/2025 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
190 | OCC_232 | AEGCL | 400KV-AZARA-BONGAIGAON-1 | D | ROUTINE TESTING OF EQUIPMENT | 23/Dec/2025 | 08:00 | 23/Dec/2025 | 16:00 | AGM MAINTENANCE MIRZA | R&U works Related Shut Down under PSDF | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon.
191 | OCC_232 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | CORRIDOR CLEANING | 20/Dec/2025 | 09:00 | 20/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed subject to 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. The voltage profile shall be maintained from SLDC ASSAM. Consent from Meghalaya is recived for maximum of 20 MW support to Hastingmari area
192 | OCC_232 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING | 20/Dec/2025 | 09:00 | 20/Dec/2025 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
193 | OCC_232 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 20/Dec/2025 | 08:00 | 20/Dec/2025 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
194 | OCC_232 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | D | LINE MAINTENANCE & CORRIODR CLEANING | 20/Dec/2025 | 08:00 | 20/Dec/2025 | 16:00 | AGM T&T NAGAON | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
195 | OCC_232 | AEGCL | 220KV-NTPS-NRPP-1 | D | CRP AND RELAY TESTING | 19/Dec/2025 | 8:30 | 19/Dec/2025 | 16:00 | RE NAMRP | R&U works Related Shut Down under PSDF | S/D may be availed. Subject to availability of 220 kV Tinsukia - NRPP line. | 08:30 to 16:00
196 | OCC_232 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING | 19/Dec/2025 | 09:00 | 19/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
197 | OCC_232 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | D | LINE MAINTENANCE & CORRIODR CLEANING | 19/Dec/2025 | 08:00 | 19/Dec/2025 | 16:00 | AGM T&T NAGAON | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
198 | OCC_232 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | D | PREVENTIVE MAINTENANCE | 18/Dec/2025 | 10:00 | 18/Dec/2025 | 13:00 | AGM SARUSAJAI | R&U works Related Shut Down under PSDF | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link. SPS for Azara-Sarusajai D/C should be kept in ON condition
199 | OCC_232 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING | 18/Dec/2025 | 09:30 | 18/Dec/2025 | 15:30 | RE LEDO | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
200 | OCC_232 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | LINE MAINTENANCE & CORRIODR CLEANING | 18/Dec/2025 | 09:00 | 18/Dec/2025 | 15:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Consent from tripura
201 | OCC_232 | AEGCL | 220KV-BTPS-RANGIA-2 | D | PREVENTIVE MAINTENANCE | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 16:00 | Sample Remarks | R&U works Related Shut Down under PSDF | S/D may be availed Subject to the availability of 220kV BTPS-Rangia ckt 1 and SPS at Rangia needs to be in ON condition
202 | OCC_232 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 17/Dec/2025 | 09:00 | 17/Dec/2025 | 16:00 | RE BOKAJAN | R&U works Related Shut Down under PSDF | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
203 | OCC_232 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING | 17/Dec/2025 | 09:00 | 17/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
204 | OCC_232 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | LINE MAINTENANCE & CORRIODR CLEANING | 17/Dec/2025 | 09:00 | 17/Dec/2025 | 15:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Consent from tripura
205 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 17/Dec/2025 | 08:00 | 17/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
206 | OCC_232 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEANING | 17/Dec/2025 | 10:00 | 17/Dec/2025 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service. | 2025-12-17
207 | OCC_232 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE | 21/Dec/2025 | 10:00 | 21/Dec/2025 | 13:00 | AGM SARUSAJAI | R&U works Related Shut Down under PSDF | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link. SPS for Azara-Sarusajai D/C should be kept in ON condition | 2025-12-21
208 | OCC_232 | AEGCL | 220KV-BTPS-RANGIA-1 | D | PREVENTIVE MAINTENANCE | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | S/D may be availed Subject to the availability of 220kV BTPS-Rangia ckt 2 and SPS at Rangia needs to be in ON condition
209 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
210 | OCC_232 | AEGCL | 400KV-AZARA-SILCHAR | D | ROUTINE TESTING OF EQUIPMENT | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 16:00 | AGM MAINTENANCE MIRZA | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 400kV Bongaigaon-Azara, 220kV Agia BTPS D/C, Salakati-BTPS D/C and 400kV Bongaiagon-Killing-Silchar link
211 | OCC_232 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING | 15/Dec/2025 | 09:30 | 15/Dec/2025 | 15:30 | RE LEDO | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
212 | OCC_232 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | CORRIDOR CLEANING | 15/Dec/2025 | 08:30 | 15/Dec/2025 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
213 | OCC_232 | AEGCL | 132KV-TINSUKIA-LEDO-1 | D | CORRIDOR CLEANING | 13/Dec/2025 | 09:30 | 13/Dec/2025 | 15:30 | RE LEDO | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132kV Tinsukia-Rupai -LEDO link.
214 | OCC_232 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING | 12/Dec/2025 | 09:00 | 12/Dec/2025 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link
215 | OCC_232 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | CORRIDOR CLEANING & JUNGLE CUTTING | 12/Dec/2025 | 09:00 | 12/Dec/2025 | 16:00 | AGM SILCHAR T&T | R&U works Related Shut Down under PSDF | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
216 | OCC_232 | AEGCL | 220KV-AGIA-AZARA-1 | D | CORRIDOR CLEANING | 12/Dec/2025 | 08:30 | 12/Dec/2025 | 16:30 | AGM T&T GOALPARA & AGM SSJI | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
217 | OCC_232 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 12/Dec/2025 | 08:00 | 12/Dec/2025 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
218 | OCC_232 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 16:00 | RE BOKAJAN | R&U works Related Shut Down under PSDF | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
219 | OCC_232 | AEGCL | 220KV-BTPS-RANGIA-2 | D | PREVENTIVE MAINTENANCE | 11/Dec/2025 | 08:00 | 11/Dec/2025 | 16:00 | Sample Remarks | R&U works Related Shut Down under PSDF | S/D may be availed Subject to the availability of 220kV BTPS-Rangia ckt 1 and SPS at Rangia needs to be in ON condition
220 | OCC_232 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 16:00 | RE GOLAGHAT | R&U works Related Shut Down under PSDF | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
221 | OCC_232 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
222 | OCC_232 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
223 | OCC_232 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING | 09/Dec/2025 | 10:00 | 09/Dec/2025 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
224 | OCC_232 | AEGCL | 220KV-AZARA-BOKO-1 | D | CORRIDOR CLEANING | 09/Dec/2025 | 08:30 | 09/Dec/2025 | 16:30 | AGM T&T GOALPARA & AGM SSJI | R&U works Related Shut Down under PSDF | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
225 | OCC_232 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & CORRIODR CLEANING | 09/Dec/2025 | 08:00 | 09/Dec/2025 | 16:00 | AGM T&T NAGAON | R&U works Related Shut Down under PSDF | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
226 | OCC_232 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 08/Dec/2025 | 09:30 | 08/Dec/2025 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
227 | OCC_232 | AEGCL | 132KV-TINSUKIA-LEDO-1 | D | CORRIDOR CLEANING | 08/Dec/2025 | 09:30 | 08/Dec/2025 | 15:30 | RE LEDO | R&U works Related Shut Down under PSDF | SD may be availed subject to the availability of 132kV Tinsukia-Rupai -LEDO link.
228 | OCC_232 | AEGCL | 220KV-BTPS-RANGIA-1 | D | PREVENTIVE MAINTENANCE | 08/Dec/2025 | 08:00 | 08/Dec/2025 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | S/D may be availed Subject to the availability of 220kV BTPS-Rangia ckt 2 and SPS at Rangia needs to be in ON condition
229 | OCC_232 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & CORRIODR CLEANING | 08/Dec/2025 | 08:00 | 08/Dec/2025 | 16:00 | AGM T&T NAGAON | R&U works Related Shut Down under PSDF | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
230 | OCC_232 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING | 06/Dec/2025 | 09:00 | 06/Dec/2025 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
231 | OCC_232 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING | 06/Dec/2025 | 09:00 | 06/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. Under N-1 contingency involving the Agia–BTPS-1 line, the combined loading on the 400/220 kV ICTs at Azara reaches approximately 470 MW, resulting in a violation of N-1 compliance at Azara. To mitigate , the combined loading on Azara ICTs should be restricted to below 380 MW under such conditions.
232 | OCC_232 | AEGCL | 132KV-HAFLONG-HAFLONG-1 | D | CORRIDOR CLEANING & JUNGLE CUTTING | 06/Dec/2025 | 06:00 | 06/Dec/2025 | 10:00 | AGM SILCHAR T&T | R&U works Related Shut Down under PSDF | SD may be availed.
233 | OCC_232 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 06/Dec/2025 | 06:00 | 06/Dec/2025 | 09:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | S/D may be availed.132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. The availability of generation from Leshka will support real-time grid operation during shutdown period. Consent from Meghalaya
234 | OCC_232 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 05/Dec/2025 | 08:30 | 05/Dec/2025 | 16:30 | AGM SARUSAJAI | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
235 | OCC_232 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING | 04/Dec/2025 | 10:00 | 04/Dec/2025 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
236 | OCC_232 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD May be availed subject to availability of 132 kV Panchgram - Lumshnong, 132 kV Panchgram - Badarpur.
237 | OCC_232 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:00 | RE GOLAGHAT | R&U works Related Shut Down under PSDF | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
238 | OCC_232 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | CORRIDOR CLEANING & JUNGLE CUTTING | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:00 | AGM SILCHAR T&T | R&U works Related Shut Down under PSDF | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
239 | OCC_232 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING | 05/Dec/2025 | 09:00 | 05/Dec/2025 | 15:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. Under N-1 contingency involving the Agia–BTPS-2 line, the combined loading on the 400/220 kV ICTs at Azara reaches approximately 470 MW, resulting in a violation of N-1 compliance at Azara. To mitigate , the combined loading on Azara ICTs should be restricted to below 380 MW under such conditions. | 2025-12-05
240 | OCC_232 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
241 | OCC_232 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 03/Dec/2025 | 09:30 | 03/Dec/2025 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
242 | OCC_232 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | D | CORRIDOR CLEANING | 03/Dec/2025 | 08:30 | 03/Dec/2025 | 16:30 | AGM SARUSAJAI | R&U works Related Shut Down under PSDF | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
243 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 03/Dec/2025 | 08:00 | 03/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
244 | OCC_232 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
245 | OCC_232 | AEGCL | MISA - 220KV - BUS 2 | D | SHIFTING OF DISMANTLED MATERIAL TO STORE YARD & MOVEMENT OF HYDRA | 10/Dec/2025 | 07:00 | 10/Dec/2025 | 16:00 | AGM SAMAGURI | Existing System Improvement Related Shut Down | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri link. All elements must be shifted to Bus before taking the SD. SPS related to tripping of 220kV Misa-Samaguri D/C to be kept on if the combined loading of both the circuit is grater than 230 MW.Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Maximum 3 units of Kopili to be scheduled during S/D period considering n-1 contingency of other bus. If 3 machines of Kopili are scheduled then maximum generation of Leshka should be less than 80 MW.
246 | OCC_232 | AEGCL | MISA - 220KV - BUS 2 | D | DISMANTLING OF CT CV, WAVETRAP, LA | 09/Dec/2025 | 07:00 | 09/Dec/2025 | 16:00 | AGM SAMAGURI | Existing System Improvement Related Shut Down | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri link. All elements must be shifted to Bus before taking the SD. SPS related to tripping of 220kV Misa-Samaguri D/C to be kept on if the combined loading of both the circuit is grater than 230 MW.Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Maximum 3 units of Kopili to be scheduled during S/D period considering n-1 contingency of other bus. If 3 machines of Kopili are scheduled then maximum generation of Leshka should be less than 80 MW.
247 | OCC_232 | AEGCL | MISA - 220KV - BUS 2 | D | DISMANTLING OF ISOLATOR, CB | 08/Dec/2025 | 07:00 | 08/Dec/2025 | 16:00 | AGM SAMAGURI | Existing System Improvement Related Shut Down | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri link. All elements must be shifted to Bus before taking the SD. SPS related to tripping of 220kV Misa-Samaguri D/C to be kept on if the combined loading of both the circuit is grater than 230 MW.Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Maximum 3 units of Kopili to be scheduled during S/D period considering n-1 contingency of other bus. If 3 machines of Kopili are scheduled then maximum generation of Leshka should be less than 80 MW.
248 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-II at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
249 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-II at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
250 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-II at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
251 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-II at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
252 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-I at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
253 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-I at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
254 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-I at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
255 | OCC_232 | NEEPCO | 400KV/132KV RANGANADI-ICT-1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV, 360 MVA ICT-I at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
256 | OCC_232 | NEEPCO | MAIN BAY (GIS) OF BR-1 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV, 80 MVAR GIS Bus Reactor at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed
257 | OCC_232 | NEEPCO | MAIN BAY (GIS) OF BR-1 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV, 80 MVAR GIS Bus Reactor at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed
258 | OCC_232 | NEEPCO | MAIN BAY (GIS) OF BR-1 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV, 80 MVAR GIS Bus Reactor at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed
259 | OCC_232 | NEEPCO | MAIN BAY (GIS) OF BR-1 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV, 80 MVAR GIS Bus Reactor at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed
260 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-B is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
261 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-B is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
262 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-B is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
263 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 2 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-B is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
264 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-A is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
265 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-A is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
266 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-A is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
267 | OCC_232 | NEEPCO | RANGANADI - 400KV - BUS 1 | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of Ranganadi 400 kV Bus-A is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. Low voltage will arise in the Ziro area. Loading of ziro area needs to be kept under 50 MW.
268 | OCC_232 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-II Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 1. Considering 400KV RANGANADI-BNC 1 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
269 | OCC_232 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-II Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 1. Considering 400KV RANGANADI-BNC 1 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
270 | OCC_232 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-II Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 1. Considering 400KV RANGANADI-BNC 1 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
271 | OCC_232 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-II Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 1. Considering 400KV RANGANADI-BNC 1 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
272 | OCC_232 | NEEPCO | 400 KV BNC 1 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-I Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 2 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
273 | OCC_232 | NEEPCO | 400 KV BNC 1 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-I Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 2 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
274 | OCC_232 | NEEPCO | 400 KV BNC 1 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-I Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 2 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
275 | OCC_232 | NEEPCO | 400 KV BNC 1 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV BNC-I Bay at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 2 as N-1 contigent Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
276 | OCC_232 | NEEPCO | BUS COUPLER BAY (402) OF RANGANADI - 400KV - BUS 1 AND RANGANADI - 400KV - BUS 2 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 14:00 | Shutdown of 400 kV Bus Coupler at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed
277 | OCC_232 | NEEPCO | BUS COUPLER BAY (402) OF RANGANADI - 400KV - BUS 1 AND RANGANADI - 400KV - BUS 2 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 10/Dec/2025 | 09:00 | 10/Dec/2025 | 14:00 | Shutdown of 400 kV Bus Coupler at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed
278 | OCC_232 | NEEPCO | BUS COUPLER BAY (402) OF RANGANADI - 400KV - BUS 1 AND RANGANADI - 400KV - BUS 2 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 14:00 | Shutdown of 400 kV Bus Coupler at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed
279 | OCC_232 | NEEPCO | BUS COUPLER BAY (402) OF RANGANADI - 400KV - BUS 1 AND RANGANADI - 400KV - BUS 2 @RANGANADI - 400KV | D | Complete Day time shutdown of 400 kV Switchyard elements are required in order to conduct 400 kV Busbar Stability Test. | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 14:00 | Shutdown of 400 kV Bus Coupler at Ranganadi is required from 08.12.2025 to 11.12.2025 on a daytime shutdown basis for 5(Five) hours from 09:00 Hrs to 14:00 Hrs. |  | SD may be availed
280 | OCC_232 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | C | Replacement of 400 kV Circuit Breaker on 400 kV BNC-II Bay at Ranganadi. | 01/Dec/2025 | 08:00 | 07/Dec/2025 | 23:00 | Shutdown of BNC-II Bay at Ranganadi is required for replacement of 400 kV Circuit Breaker from 01.12.2025 08:00 Hrs to 07.12.2025 23:00 Hrs on a continuous basis. | Existing System Improvement Related Shut Down | SD may be availed subjected to the availability of 400kV BNC-Ranganadi-2, 400/132kV 200 MVA ICTs at BNC and 132kV BNC(PG)-Chimpu link. FTC procedure to be followed
281 | OCC_232 | NEEPCO | RANGANADI - UNIT 2 | C | Annual Planned Maintenance of Ranganadi Generating Unit-02 | 05/Dec/2025 | 08:00 | 25/Dec/2025 | 23:00 | Shutdown of Ranganadi Generating Unit-02 is required for APM works from 05.12.2025 08:00 Hrs to 25.12.2025 23:00 Hrs on a continuous basis. | Existing System Normal Maintenance Related Shut Down | Sd may be availed, consent of benefiary is required.
282 | OCC_232 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Maintenance Work | 21/Dec/2025 | 09:00 | 21/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability 9of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
283 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 31/Dec/2025 | 07:00 | 31/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
284 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 30/Dec/2025 | 07:00 | 30/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
285 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 29/Dec/2025 | 07:00 | 29/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
286 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 28/Dec/2025 | 07:00 | 28/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
287 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 27/Dec/2025 | 07:00 | 27/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
288 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 26/Dec/2025 | 07:00 | 26/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
289 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 25/Dec/2025 | 07:00 | 25/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
290 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 24/Dec/2025 | 07:00 | 24/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
291 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 23/Dec/2025 | 07:00 | 23/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
292 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 22/Dec/2025 | 07:00 | 22/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
293 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 21/Dec/2025 | 07:00 | 21/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
294 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 20/Dec/2025 | 07:00 | 20/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
295 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 19/Dec/2025 | 07:00 | 19/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
296 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 18/Dec/2025 | 07:00 | 18/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
297 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 17/Dec/2025 | 07:00 | 17/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
298 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 16/Dec/2025 | 07:00 | 16/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
299 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 15/Dec/2025 | 07:00 | 15/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
300 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 14/Dec/2025 | 07:00 | 14/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
301 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 13/Dec/2025 | 07:00 | 13/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
302 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 12/Dec/2025 | 07:00 | 12/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
303 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 11/Dec/2025 | 07:00 | 11/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
304 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 10/Dec/2025 | 07:00 | 10/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
305 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 09/Dec/2025 | 07:00 | 09/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
306 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 08/Dec/2025 | 07:00 | 08/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
307 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 07/Dec/2025 | 07:00 | 07/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
308 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 06/Dec/2025 | 07:00 | 06/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
309 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 05/Dec/2025 | 07:00 | 05/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
310 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 04/Dec/2025 | 07:00 | 04/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
311 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 03/Dec/2025 | 07:00 | 03/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
312 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 02/Dec/2025 | 07:00 | 02/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
313 | OCC_232 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Reconductoring works | 01/Dec/2025 | 07:00 | 01/Dec/2025 | 16:00 |  |  | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
314 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 31/Dec/2025 | 07:00 | 31/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
315 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 30/Dec/2025 | 07:00 | 30/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
316 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 29/Dec/2025 | 07:00 | 29/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
317 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 28/Dec/2025 | 07:00 | 28/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
318 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 27/Dec/2025 | 07:00 | 27/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
319 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 26/Dec/2025 | 07:00 | 26/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
320 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 25/Dec/2025 | 07:00 | 25/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
321 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 24/Dec/2025 | 07:00 | 24/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
322 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 23/Dec/2025 | 07:00 | 23/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
323 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 22/Dec/2025 | 07:00 | 22/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
324 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 21/Dec/2025 | 07:00 | 21/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
325 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 20/Dec/2025 | 07:00 | 20/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
326 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 19/Dec/2025 | 07:00 | 19/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
327 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 18/Dec/2025 | 07:00 | 18/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
328 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 17/Dec/2025 | 07:00 | 17/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
329 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 16/Dec/2025 | 07:00 | 16/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
330 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 15/Dec/2025 | 07:00 | 15/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
331 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 14/Dec/2025 | 07:00 | 14/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
332 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 13/Dec/2025 | 07:00 | 13/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
333 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 12/Dec/2025 | 07:00 | 12/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
334 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 11/Dec/2025 | 07:00 | 11/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
335 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 10/Dec/2025 | 07:00 | 10/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
336 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 09/Dec/2025 | 07:00 | 09/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.FTC procedure to be followed before final charging of the line
337 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 08/Dec/2025 | 07:00 | 08/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
338 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 07/Dec/2025 | 07:00 | 07/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
339 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 06/Dec/2025 | 07:00 | 06/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
340 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 05/Dec/2025 | 07:00 | 05/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
341 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 04/Dec/2025 | 07:00 | 04/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
342 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 03/Dec/2025 | 07:00 | 03/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
343 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 02/Dec/2025 | 07:00 | 02/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
344 | OCC_232 | TSECL | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | Reconductoring works | 01/Dec/2025 | 07:00 | 01/Dec/2025 | 16:00 |  |  | S/D may be availed subject to 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present. FTC procedure to be followed
345 | OCC_232 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Maintenance Work | 18/Dec/2025 | 09:00 | 18/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
346 | OCC_232 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Maintenance Work | 11/Dec/2025 | 09:00 | 11/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
347 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Maintenance Work | 23/Dec/2025 | 09:00 | 23/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
348 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Maintenance Work | 20/Dec/2025 | 09:00 | 20/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
349 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Maintenance Work | 09/Dec/2025 | 09:00 | 09/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW. | SD deffered due to SD of 132kV Monarchak udaipur line
350 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Maintenance Work | 06/Dec/2025 | 09:00 | 06/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | S/D may be availed 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW. | SD deffered due to SD of 132kV Monarchak udaipur line
351 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Maintenance Work | 22/Dec/2025 | 09:00 | 22/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
352 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Maintenance Work | 19/Dec/2025 | 09:00 | 19/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
353 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Maintenance Work | 15/Dec/2025 | 09:00 | 15/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 132kV SM Nagar(ISTS)-Budhjungnagar and 132kV Surajmaninagar(TSECL)-Budhjungnagar
354 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Maintenance Work | 08/Dec/2025 | 09:00 | 08/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW. | SD deffered due to SD of 132kV Monarchak udaipur line
355 | OCC_232 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Maintenance Work | 04/Dec/2025 | 09:00 | 04/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | S/D may be availed 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW. | SD deffered due to SD of 132kV Monarchak udaipur line
356 | OCC_232 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Maintenance Work | 16/Dec/2025 | 09:00 | 16/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
357 | OCC_232 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Maintenance Work | 02/Dec/2025 | 09:00 | 02/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
358 | OCC_232 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Maintenance Work | 13/Dec/2025 | 09:00 | 13/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability 9of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
359 | OCC_232 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Maintenance Work | 07/Dec/2025 | 09:00 | 07/Dec/2025 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability 9of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
360 | OCC_232 | NETCL | 400KV-PALATANA-SILCHAR-2 | D | Rectification of Jumper, CC Ring, Grading Ring, Tightening/ Replacement of Loose/ Rusted N&B etc. | 05/Dec/2025 | 11:00 | 05/Dec/2025 | 13:00 | Put up for approval in the 232nd OCCM. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 400kV Palatana-Silchar 1, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
361 | OCC_232 | NETCL | 400KV-PALATANA-SILCHAR-1 | D | Rectification of Jumper, CC ring, Grading ring, tightening of loose N&B, Replacement of rusted N&B etc. | 04/Dec/2025 | 11:00 | 04/Dec/2025 | 13:00 | Put up for approval in the 232nd OCCM. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the availability of 400kV Palatana-Silchar 2, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
362 | OCC_232 | NEEPCO | HRSG - 3 OF AGTCCPP (STG UNIT 6) - UNIT 6 | C | Hydro Test of HRSG - 3 | 13/Dec/2025 | 00:00 | 19/Dec/2025 | 23:59 | Statutory Test | Existing System Normal Maintenance Related Shut Down | Sd may be availed, consent of benefiary is required.
363 | OCC_232 | MEPTCL | UMTRU - 132KV - BUS 1 | D | Preventive maintenance work on terminal equipment Viz. line side isolator contact, isolator, clamp, CT clamp. CBs, breaker clamp, replacement of damaged jumper,etc. Also annual testing of Protection System, GTs & Switching equipment as requested by EE(GSPD) shall be considered incorporated in the same schedule. | 05/Dec/2025 | 09:00 | 05/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of Killing-EPIP-EPIP 2-New Umtru link, Khleiriat-Khleiriat D/C-Neighrims-Mustem-Nehu Umiam I link , Nehu-Mawlai-Mawngap link needs to be present. Consent from Assam is required
364 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Preventive Maintenance BUS B isolator (210 89B) | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#1,ICT#3, Misa 1 and Mawngap 1) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-1, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
365 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Preventive Maintenance BUS B isolator (205 89B) | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#1,ICT#3, Misa 1 and Mawngap 1) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
366 | OCC_232 | MEPTCL | 400KV/220KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance BUS B isolator (208 89B) | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#1,ICT#3, Misa 1 and Mawngap 1) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may availed subject to the availability of 400/220kV ICT 1 at Killing and 220kV Misa-Killing D/C
367 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance BUS B isolator (206 89B) | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#1,ICT#3, Misa 1 and Mawngap 1) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 1 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
368 | OCC_232 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 2 | D | Preventive Maintenance BUS B isolator | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#1,ICT#3, Misa 1 and Mawngap 1) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
369 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Preventive Maintenance BUS B isolator (209 89B) | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
370 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Preventive Maintenance BUS B isolator (204 89B) | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
371 | OCC_232 | MEPTCL | 400KV/220KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance BUS B isolator (207 89B) | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may availed subject to the availability of 400/220kV ICT 2 at Killing and 220kV Misa-Killing D/C
372 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance BUS B isolator (203 89B) | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 2 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
373 | OCC_232 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 2 | D | Preventive Maintenance BUS B isolator (201 89A) | 16/Dec/2025 | 08:00 | 16/Dec/2025 | 15:00 | 220Kv Bus A and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2) will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
374 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance of Terminal Equipments LV bay and ICT, Testing of ICT#2 by MRT | 12/Dec/2025 | 08:00 | 12/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 1 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
375 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance of Terminal Equipments HV bay and ICT, Testing of ICT#2 by MRT | 13/Dec/2025 | 08:00 | 13/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 1 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link. | 2025-12-13
376 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance of Terminal Equipments LV bay and ICT, Testing of ICT#1 by MRT | 10/Dec/2025 | 08:00 | 10/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 2 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
377 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance of Terminal Equipments HV bay and ICT, Testing of ICT#1 by MRT. | 09/Dec/2025 | 08:00 | 09/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 2 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
378 | OCC_232 | MEPTCL | 400KV/220KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance of LV Side BUS A isolator (208 89A) | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder ( ICT#1, ICT#3, Misa 1 and Mawngap 1 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may availed subject to the availability of 400/220kV ICT 1 at Killing and 220kV Misa-Killing D/C
379 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-2 | D | Preventive Maintenance of ICT#2 BUS A isolator (206 89A | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder ( ICT#1, ICT#3, Misa 1 and Mawngap 1 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 1 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
380 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Preventive Maintenance of Mawngap 2 BUS A isolator (210 89A) | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder ( ICT#1, ICT#3, Misa 1 and Mawngap 1 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-1, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
381 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Preventive Maintenance of Misa 2 BUS A isolator (205 89A) | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder ( ICT#1, ICT#3, Misa 1 and Mawngap 1 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
382 | OCC_232 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 1 | D | Preventive Maintenance of BUS A Isolator | 04/Dec/2025 | 08:00 | 04/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder ( ICT#1, ICT#3, Misa 1 and Mawngap 1 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
383 | OCC_232 | MEPTCL | 400KV/220KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance of LV Side BUS A isolator( 207 89A) | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may availed subject to the availability of 400/220kV ICT 2 at Killing and 220kV Misa-Killing D/C
384 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Preventive Maintenance of Mawngap 1 BUS A isolator (209 89A) | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
385 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Preventive Maintenance of Misa 1 BUS A isolator (204 89A) | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
386 | OCC_232 | MEPTCL | 220KV/132KV BYRNIHAT (KILLING) -ICT-1 | D | Preventive Maintenance of ICT#1 BUS A isolator (203 89A) | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 200/132 kV ICT 2 at Killing, 220kV Killing-Mawngap-Umiam I-Umtru-Epip link.
387 | OCC_232 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 1 | D | Maintenance of busbar | 02/Dec/2025 | 08:00 | 02/Dec/2025 | 15:00 | 220Kv Bus B and all other feeder( ICT#2,ICT#4, Misa 2 and Mawngap 2 will be in service. Bus Coupler will be in open condition. | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
388 | OCC_232 | MEPTCL | KHLIEHRIAT(ME) - 132KV - BUS 1 | D | Maintenance of the BSI of Y-phase of 132KV Lumshnong Bus side and R-phase of PG Line-II | 07/Dec/2025 | 10:00 | 07/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | S/D may be availed Subject to the availability of 132kV Panchgram-Lumshnong link, 220kV Killing-Mawngap D/C and 220/132kV ICTs at Mawngap, 132kV Killing-EPIP-1-Epip 2-Umtru, 132kV Killing-EPIP-1-Epip 2-newUmtru-Umtru-Umian III-Umiam I link, 132kv Umiam I - Umiam(loading to be mainated under 55 MW), 132kV Umiam I-Mawlai(loading to be maintained under 35 MW). Khandong -kopili-misa link needs to be present. | 2025-12-07
389 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Maintenance works | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
390 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Maintenance works | 18/Dec/2025 | 08:00 | 18/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
391 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Maintenance works | 17/Dec/2025 | 08:00 | 17/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
392 | OCC_232 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Maintenance works | 17/Dec/2025 | 08:00 | 17/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
393 | OCC_232 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | D | Maintenance works | 10/Dec/2025 | 08:00 | 10/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
394 | OCC_232 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | D | Maintenance works | 10/Dec/2025 | 08:00 | 10/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
395 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | S/D from T/Loc No. 148 at Lawsiej to T/Loc No. 262 at Mawphlang. For tightening of nuts & bolts at T/Loc No. 186-190 | 11/Dec/2025 | 08:30 | 11/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
396 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | S/D from T/Loc No. 148 at Lawsiej to T/Loc No. 262 at Mawphlang. For tightening of nuts & bolts at T/Loc No. 186-190 | 11/Dec/2025 | 08:30 | 11/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-1, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
397 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | S/D from T/Loc No. 148 at Lawsiej to T/Loc No. 262 at Mawphlang. For tightening of nuts & bolts at T/Loc No. 179-185 | 05/Dec/2025 | 08:30 | 05/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
398 | OCC_232 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | S/D from T/Loc No. 148 at Lawsiej to T/Loc No. 262 at Mawphlang. For tightening of nuts & bolts at T/Loc No. 179-185 | 05/Dec/2025 | 08:30 | 05/Dec/2025 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to availability of 220KV-MAWNGAP-BYRNIHAT (KILLING)-1, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
399 | OCC_232 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | D | Jungle Clearance T/Loc 281-290 | 12/Dec/2025 | 09:00 | 12/Dec/2025 | 14:00 | Avail | Existing System Normal Maintenance Related Shut Down | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra.
400 | OCC_232 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Jungle Clearance T/Loc 236-238 & 242-248 | 08/Dec/2025 | 08:00 | 08/Dec/2025 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | S/D may be availed Subject to the availability of 132kV Mendipathar-Agia, 132kV Mendipathar-Nangalbibra.
401 | OCC_232 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Replacement of Broken Disc (R-Phase) at T/Loc.106 | 03/Dec/2025 | 10:00 | 03/Dec/2025 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed
402 | OCC_232 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | D | Preventive maintenance work on terminal equipment Viz. line side isolator contact, isolator, clamp, CT clamp. CBs, breaker clamp, replacement of damaged jumper,etc. Also annual testing of Protection System, GTs & Switching equipment as requested by EE(GSPD) shall be considered incorporated in the same schedule. | 03/Dec/2025 | 14:00 | 03/Dec/2025 | 19:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
403 | OCC_232 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | D | Preventive maintenance work on terminal equipment Viz. line side isolator contact, isolator, clamp, CT clamp. CBs, breaker clamp, replacement of damaged jumper,etc. Also annual testing of Protection System, GTs & Switching equipment as requested by EE(GSPD) shall be considered incorporated in the same schedule. | 03/Dec/2025 | 09:00 | 03/Dec/2025 | 13:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
404 | OCC_232 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | D | Preventive maintenance work on terminal equipment Viz. line side isolator contact, isolator, clamp, CT clamp. CBs, breaker clamp, replacement of damaged jumper,etc. Also annual testing of Protection System, GTs & Switching equipment as requested by EE(GSPD) shall be considered incorporated in the same schedule. | 02/Dec/2025 | 14:00 | 02/Dec/2025 | 19:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
405 | OCC_232 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | D | Preventive maintenance work on terminal equipment Viz. line side isolator contact, isolator, clamp, CT clamp. CBs, breaker clamp, replacement of damaged jumper,etc. Also annual testing of Protection System, GTs & Switching equipment as requested by EE(GSPD) shall be considered incorporated in the same schedule. | 02/Dec/2025 | 09:00 | 02/Dec/2025 | 13:00 | Avail | Existing System Normal Maintenance Related Shut Down | SD may be availed, intimation to SLDC Assam
406 | OCC_232 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | D | Monthly change over of 3x105MVA transformer (R,Y &SPHER phase ICTs will be charged) | 04/Dec/2025 | 11:00 | 04/Dec/2025 | 13:00 | no load will be affected during the shutdown | Existing System Normal Maintenance Related Shut Down | SD may be availed subject to the Imphal-Yurembam-Yiangangpopki-KongbaThubal-kakching-Churachandpur-Ningthoukhong link.
407 | OCC_232 | NEEPCO | KOPLII - UNIT 3 | C | Annual Planned maintenance | 16/Dec/2025 | 00:00 | 31/Dec/2025 | 00:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed. Consent of beneficiary is required.
408 | OCC_232 | NEEPCO | KOPLII - UNIT 4 | C | Annual Planned maintenance | 01/Dec/2025 | 00:00 | 16/Dec/2025 | 00:00 |  | Existing System Normal Maintenance Related Shut Down | SD may be availed. Consent of beneficiary is required.
Outages proposed in other RPCs requiring NERPC approval
Sl No | Outages proposed in | Name of Requesting Agency | Name of Elements | From |  | TO |  | Basis | Reason | Remarks (If Any)
|  |  |  | Date | Time | Date | Time
1 | cpcc3_sd | NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | 2025-12-22 | 08:00 | 2025-12-22 | 20:00 | D | AMP works of pole-3 neutral area WB3 | Subjected to ERPC approval. To be clubbed with line diversion work.
2 | cpcc3_sd | NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | 2025-12-11 | 08:00 | 2025-12-11 | 20:00 | D | AMP works of pole-2&4 common neutral area WB2,WB4 | Subjected to ERPC approval. To be clubbed with line diversion work.
3 | cpcc3_sd | NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | 2025-12-06 | 08:00 | 2025-12-15 | 18:00 | C | Line Diversion work due to construction of Lucknow-Kanpur Green Expressway Work by NHAI.All 4 Pole will be out | Subjected to ERPC approval. All 4 poles will be out.
4 | cpcc3_sd | NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | 2025-12-06 | 08:00 | 2025-12-15 | 18:00 | C |  | Subjected to ERPC approval. All 4 poles will be out.
5 | cpcc3_sd | NRPC | 800 KV HVDC AGRA(PG) POLE-4 | 2025-12-15 | 08:00 | 2025-12-17 | 20:00 | D | AMP works of Pole-4 Converter transformer and converter bay | Subjected to ERPC approval. To be clubbed with line diversion work.
6 | cpcc3_sd | NRPC | 800 KV HVDC AGRA(PG) POLE-2 | 2025-12-08 | 08:00 | 2025-12-10 | 20:00 | D | AMP works of Pole-2 Converter transformer and pole neutral area | Subjected to ERPC approval. To be clubbed with line diversion work.
7 | cpcc3_sd | NRPC | 800 KV HVDC AGRA(PG) POLE-3 | 2025-12-01 | 08:00 | 2025-12-02 | 22:00 | D | RTV coating work on HVDC Pole-3 DC Hall insulators. | Subjected to ERPC approval. To be clubbed with line diversion work.