## Sheet1
Sl. no | OCC number | Name of requesting agency | Element name | Daily/ Continous | Reason | Shutdown start date | Shutdown start time | Shutdown end date | Shutdown end time | Request type | Tag | Reference number | Study comments
1 | OCC_234 | NEEPCO | DOYANG - UNIT 2 | C | Installation and commissiong of New 28.5 MVA GT and APM works | 16/Feb/2026 | 00:00 | 28/Feb/2026 | 23:59 | Shutdown duration from 16-02-2026 00:00 Hrs to 25-03-2026 23:59 Hrs | Existing System Normal Maintenance Related Shut Down | RQ30620 | SD may be availed. Consent from Beneficiaries is required.
2 | OCC_234 | PENTL | NAMSAI - 220KV B/R 1 | D | Commisioning of ODS system | 06/Feb/2026 | 8:00 | 06/Feb/2026 | 16:00 | PLANNED | Contruction | RQ30612 | Shutdown may be availed
3 | OCC_234 | POWERGRID | 400 KV BGTPP 1 BAY AT BONGAIGAON | C | CB MECHANISM OVERHAULING WORKS | 23/Feb/2026 | 8:00 | 26/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30589 | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon I & 400kV Byrnihat - Bongaigaon tie bay and 400kV 400kV Byrnihat - Bongaigaon main bay at 400kV Bongaigaon S/S
4 | OCC_234 | POWERGRID | BUS COUPLER BAY (1) OF MISA - 220KV - BUS 1 AND MISA - 220KV - BUS 2 @MISA - 220KV | D | AMP works | 23/Feb/2026 | 8:00 | 23/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30608 | Sd may be availed subject to no outage of elements
5 | OCC_234 | POWERGRID | BUS COUPLER BAY () OF SILCHAR - 132KV - BUS 1 AND SILCHAR - 132KV - BUS 2 @SILCHAR - 132KV | D | AMP works | 23/Feb/2026 | 8:00 | 23/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30609 | Sd may be availed subject to no outage of elements
6 | OCC_234 | POWERGRID | TIE BAY () OF 400KV-BALIPARA-BONGAIGAON-4 AND 400KV-BALIPARA-KAMENG-1 @BALIPARA - 400KV | C | CB MECHANISM OVERHUALING WORKS | 23/Feb/2026 | 8:00 | 26/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30611 | SD may be availed subject to availability of 400kV Balipara - Bongaigaon IV main bay and 400kV Balipara - Kameng I main bay at 400kV Balipara S/S
7 | OCC_234 | POWERGRID | TIE BAY () OF 400KV-PALATANA-SILCHAR-1 AND SILCHAR - 400KV B/R 2 @SILCHAR - 400KV | C | CB MECHANISM OVERHAULING WORKS | 19/Feb/2026 | 8:00 | 21/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30605 | SD may be availed subject to availability of 400kV Palatan - Silchar I main bay and 400kV BR2 main bay at 400kV Silchar S/S
8 | OCC_234 | POWERGRID | TIE BAY () OF 400KV-BALIPARA-BONGAIGAON-3 AND 400KV-BALIPARA-KAMENG-2 @BALIPARA - 400KV | C | CB MECHANISM OVERHUALING WORKS | 19/Feb/2026 | 8:00 | 22/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30606 | SD may be availed subject to no outage of elements.
9 | OCC_234 | POWERGRID | 400 KV, 80 MVAR BUS REACTOR 3 BAY AT BONGAIGAON | C | CB MECHANISM OVERHAULING WORKS | 19/Feb/2026 | 8:00 | 22/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30610 | SD may be availed subject to outage of no elements ( Bus reactor 3 and 4 at Bongaiagon share the same bay. Shares the dia with BTPS ckt 2)
10 | OCC_234 | POWERGRID | MAIN BAY () OF 400KV-BALIPARA-KAMENG-2 @BALIPARA - 400KV | C | CB MECHANISM OVERHUALING WORKS | 15/Feb/2026 | 8:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30602 | Sd may be availed subject to availability of 400kV Balipara - Bongaigaon III main bay and 400kV Balipara - Kameng II & 400kV Balipara - Bongaigaon III tie bay at 400kV Balipara S/S
11 | OCC_234 | POWERGRID | BTPS(NTPC) II (FUTURE) & 2X 80 MVAR BUS REACTOR III AND IVAT BONGAIGAON | C | CB MECHANISM OVERHAULING WORKS | 15/Feb/2026 | 8:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30603 | SD may be availed subject to the availability of NTPC- Bongaigaon ckt 2 and Ckt 1 must be charged though main bay
12 | OCC_234 | POWERGRID | TIE BAY () OF 400KV-BISWANATH CHARIALI-RANGANADI-2 AND BISWANATH CHARIALI - 400KV B/R 2 @BISWANATH CHARIALI - 400KV | C | CB MECHANISM OVERHUALING WORKS | 15/Feb/2026 | 8:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30604 | SD may be availed subject to no outage of elements.
13 | OCC_234 | POWERGRID | TIE BAY (408) OF 400KV-MISA-MARIANI (PG)-1 AND 400KV/220KV MARIANI (PG)-ICT-2 @MARIANI (PG) - 400KV | D | AMP works | 14/Feb/2026 | 8:00 | 14/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30601 | SD may availed subject to availability of 400kV Misa - Mariani(PG) 1 main bay and 400/220kV Marinai Ict-2 main bay at 400kV Mariani(PG) S/S
14 | OCC_234 | POWERGRID | MAIN BAY (403) OF MARIANI (PG) - 400KV B/R 1 AND @MARIANI (PG) - 400KV | D | AMP works | 12/Feb/2026 | 8:00 | 12/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30600 | SD may be availed
15 | OCC_234 | POWERGRID | MAIN BAY () OF 400KV-BALIPARA-KAMENG-1 @BALIPARA - 400KV | C | CB MECHANISM OVERHUALING WORKS | 11/Feb/2026 | 8:00 | 14/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30598 | SD may be availed subject to the availability of 400kV Balipara - Bongaigaon IV main bay and 400kV Balipara - Kameng I & 400kV Balipra - Bongaigaon IV tie bay Balipara
16 | OCC_234 | POWERGRID | TIE BAY (W17Q2) OF 400KV-BISWANATH CHARIALI-RANGANADI-1 AND 400KV-BISWANATH CHARIALI-BALIPARA-1 @BISWANATH CHARIALI - 400KV | C | CB MECHANISM OVERHUALING WORKS | 11/Feb/2026 | 8:00 | 14/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30599 | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1 Main Bay AND 400KV-BISWANATH CHARIALI-BALIPARA-1 Main Bay 400kV BNC
17 | OCC_234 | POWERGRID | TIE BAY (402) OF MARIANI (PG) - 400KV B/R 1 AND FUTURE @MARIANI (PG) - 400KV | D | AMP works | 10/Feb/2026 | 8:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30596 | SD may be availed
18 | OCC_234 | POWERGRID | 400 KV BGTPP 2 BAY AT BONGAIGAON | C | CB MECHANISM OVERHAULING WORKS | 10/Feb/2026 | 8:00 | 13/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30597 | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon II & 80MVAR BR III, IV tie bay and 80 MVAR BR III, IV main bay at Bogaingaon
19 | OCC_234 | POWERGRID | MAIN (1) BAY OF 400KV/220KV MISA-ICT-2 @MISA - 400KV | C | CB MECHANISM OVERHAULING WORKS | 09/Feb/2026 | 8:00 | 12/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30595 | SD may be availed subject to availability of ICT 1 and 3 at Misa
20 | OCC_234 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | D | AMP WORKS | 09/Feb/2026 | 8:00 | 09/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30607 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
21 | OCC_234 | POWERGRID | 400,125 MVAR BUS REACTOR 3 BAY AT BALIPARA | C | CB MECHANISM OVERHUALING WORKS | 07/Feb/2026 | 8:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30591 | SD may be availed subject to no outage of elements. Tie bay must be in service
22 | OCC_234 | POWERGRID | BUS COUPLER BAY () OF MARIANI (PG) - 220KV - BUS 1 AND MARIANI (PG) - 220KV - BUS 2 @MARIANI (PG) - 220KV | D | AMP works | 07/Feb/2026 | 8:00 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30592 | SD may be availed subject to no outage of elements.
23 | OCC_234 | POWERGRID | 400 KV RANGANADI 1 BAY AT HVDC BNC | C | CB MECHANISM OVERHAULING WORKS | 07/Feb/2026 | 8:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30593 | SD may be availed subject to no outage of elements. Tie bay must be in service
24 | OCC_234 | POWERGRID | MAIN BAY () OF 400KV-BALIPARA-MISA-2 @MISA - 400KV | D | AMP WORKS | 07/Feb/2026 | 8:00 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30594 | SD may be availed subject to no outage of elements. Tie bay must be in service
25 | OCC_234 | POWERGRID | MAIN BAY (212) OF MARIANI (AS) - 220KV - 2 FUTURE @MARIANI (PG) - 220KV | D | AMP works | 05/Feb/2026 | 8:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30588 | SD May be availed
26 | OCC_234 | POWERGRID | MAIN (1) BAY OF 400KV-BALIPARA-MISA-1 @MISA - 400KV | D | AMP WORKS | 05/Feb/2026 | 8:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30590 | SD May be availed subject to availability of corresponding tie bay
27 | OCC_234 | POWERGRID | TRANSFER BUS COUPLER BAY (106) OF SALAKATI - 132KV - BUS 1 AND SALAKATI - 132KV - BUS 2 @SALAKATI - 132KV | D | AMP works | 04/Feb/2026 | 8:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30586 | S/d may be availed
28 | OCC_234 | POWERGRID | TIE BAY () OF 400KV-SILCHAR-IMPHAL(PG)-2 AND 400KV/132KV IMPHAL(PG)-ICT-2 @IMPHAL(PG) - 400KV | D | AMP works | 04/Feb/2026 | 8:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30587 | S/D may be availed subject to availability of main bays of 400kV Silchar-2 and ICT-2 at 400kV Imphal(PG)
29 | OCC_234 | POWERGRID | TRANSFER BUS COUPLER BAY (202) OF (SALAKATI - 220KV - BUS 1 & SALAKATI - 220KV - BUS 2) AND SALAKATI - 220KV - BUS 3 @SALAKATI - 220KV | D | AMP works | 03/Feb/2026 | 8:00 | 03/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30584 | Shutdown may be availed
30 | OCC_234 | POWERGRID | MAIN BAY (211) OF MARIANI (AS) - 220KV - 1 FUTURE @MARIANI (PG) - 220KV | D | AMP works | 03/Feb/2026 | 8:00 | 03/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30585 | Shutdown may be availed
31 | OCC_234 | POWERGRID | 400 KV BONGAIGAON 3 MAIN BAY(WITH 63 MVAR LINE REACTOR ) (419) AT BALIPARA | C | CB MECHANISM OVERHAULING WORKS | 02/Feb/2026 | 8:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30582 | Shutdown may be availed subject to availability of tie bay and kameng Unit-2 main bay at Balipara
32 | OCC_234 | POWERGRID | 400 KV RANGANADI 2 BAY AT HVDC BNC | C | CB MECHANISM OVERHAULING WORKS | 02/Feb/2026 | 8:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30583 | Shutdown may be availed subject to availability of tie bay and 80 MVAR BR2 main bay at BNC
33 | OCC_234 | POWERGRID | 400KV/220KV MARIANI (PG)-ICT-1 | D | AMP works | 19/Feb/2026 | 8:00 | 19/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30581 | Sd may be availed subject to availability of 400/220kV Mariani(PG) ICT-2
34 | OCC_234 | POWERGRID | 220KV/132KV SALAKATI-ICT-1 | C | Aircell replacment in ICT | 11/Feb/2026 | 8:00 | 13/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30579 | SD may be availed subject to the availability of other ICTs
35 | OCC_234 | POWERGRID | 400KV/220KV MISA-ICT-3 | D | Replacement of Electomechanical relay with Numerical Relay for LV OC /EF in ICT-3 with same settings at MISA Ss | 03/Feb/2026 | 6:00 | 03/Feb/2026 | 16:00 | PLANNED | Existing System Improvement Related Shut Down | RQ30580 | SD may be availed subject to the availability of 400/220 kV ICT 1 and ICT 2
36 | OCC_234 | POWERGRID | MARIANI (PG) - 400KV B/R 1 | D | AMP works | 27/Feb/2026 | 8:00 | 27/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30573 | SD may be availed
37 | OCC_234 | POWERGRID | MARIANI (PG) - 220KV B/R 1 | D | AMP works | 17/Feb/2026 | 8:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30571 | SD may be availed
38 | OCC_234 | POWERGRID | KUMARGHAT - 132KV B/R 1 | C | For offline oil filtaration works | 02/Feb/2026 | 08:00 | 08/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30572 | Shutdown may be availed
39 | OCC_234 | POWERGRID | 132KV-HAFLONG-JIRIBAM-1 | D | Tension tower jumper tightening work by Silchar TLM | 28/Feb/2026 | 08:00 | 28/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30520 | SD may be availed subjected to availability of 132kV Khandong - Umrangsho - Haflong (PG)
40 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 28/Feb/2026 | 7:00 | 28/Feb/2026 | 16:00 | PLANNED |  | RQ30568 | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-1 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
41 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR IN NON -AUTO MODE FOR REPLACMENT OF INSULATOR IN 400KV-SILCHAR-IMPHAL(PG)-2 | 28/Feb/2026 | 7:00 | 28/Feb/2026 | 16:00 | PLANNED |  | RQ30570 | Sd may be availed
42 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 27/Feb/2026 | 7:00 | 27/Feb/2026 | 16:00 | PLANNED |  | RQ30567 | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-1 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
43 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR IN NON -AUTO MODE FOR REPLACMENT OF INSULATOR IN 400KV-SILCHAR-IMPHAL(PG)-2 | 27/Feb/2026 | 7:00 | 27/Feb/2026 | 16:00 | PLANNED |  | RQ30569 | Sd may be availed
44 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 26/Feb/2026 | 7:00 | 26/Feb/2026 | 16:00 | PLANNED |  | RQ30564 | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-2 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
45 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR IN NON -AUTO MODE FOR REPLACMENT OF INSULATOR IN 400KV-SILCHAR-IMPHAL(PG)-1 | 26/Feb/2026 | 7:00 | 26/Feb/2026 | 16:00 | PLANNED |  | RQ30566 | Sd may be availed
46 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 25/Feb/2026 | 7:00 | 25/Feb/2026 | 16:00 | PLANNED |  | RQ30563 | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-2 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
47 | OCC_234 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR IN NON -AUTO MODE FOR REPLACMENT OF INSULATOR IN 400KV-SILCHAR-IMPHAL(PG)-1 | 25/Feb/2026 | 7:00 | 25/Feb/2026 | 16:00 | PLANNED |  | RQ30565 | Sd may be availed
48 | OCC_234 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-2 | D | AMP works | 20/Feb/2026 | 08:00 | 20/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30521 | Sd may be availed
49 | OCC_234 | POWERGRID | 132KV-CHAPAKHOWA-ROING-2 | D | AMP works | 18/Feb/2026 | 7:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30519 | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-2, 132kV Panyor -Ziro-Daparizo-Basar-Along-Pasighat-Roing and Roing-Tezu-Namsai-Kathalguri link
50 | OCC_234 | POWERGRID | 132KV-SILCHAR-SRIKONA-2 | D | AMP work | 18/Feb/2026 | 09:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30517 | SD may be availed subject to the availability of 132KV-SILCHAR-SRIKONA-1 and 132kV Jiribam-Pailapool-Srikona link.
51 | OCC_234 | POWERGRID | 132KV-CHAPAKHOWA-ROING-1 | D | AMP works | 17/Feb/2026 | 7:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30516 | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-2, 132kV Panyor -Ziro-Daparizo-Basar-Along-Pasighat-Roing and Roing-Tezu-Namsai-Kathalguri link
52 | OCC_234 | POWERGRID | 132KV-KHLIEHRIAT(ME)-KHELIEHRIAT-1 | D | AMP for Bay Equipment of Khliehriat(PG)_Khliehriat(MeECL)-1 Bay at Both ends. | 17/Feb/2026 | 7:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30518 | SD may be availed subject to availability of 132kV Khleihriat - Khleihriat I, 132kV Badarpur - Panchgram - Lumshnong- Khliehriat link and 220kV Killing - Mawngap D/C
53 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 17/Feb/2026 | 7:00 | 17/Feb/2026 | 16:00 | PLANNED |  | RQ30547 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
54 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 16/Feb/2026 | 7:00 | 16/Feb/2026 | 16:00 | PLANNED |  | RQ30546 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
55 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 15/Feb/2026 | 7:00 | 15/Feb/2026 | 16:00 | PLANNED |  | RQ30545 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
56 | OCC_234 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 15/Feb/2026 | 7:00 | 15/Feb/2026 | 16:00 | PLANNED |  | RQ30560 | SD deferred
57 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 14/Feb/2026 | 7:00 | 14/Feb/2026 | 16:00 | PLANNED |  | RQ30544 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
58 | OCC_234 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 14/Feb/2026 | 7:00 | 14/Feb/2026 | 16:00 | PLANNED |  | RQ30559 | SD deferred
59 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 13/Feb/2026 | 7:00 | 13/Feb/2026 | 16:00 | PLANNED |  | RQ30543 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
60 | OCC_234 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 13/Feb/2026 | 7:00 | 13/Feb/2026 | 16:00 | PLANNED |  | RQ30558 | SD deferred
61 | OCC_234 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/Feb/2026 | 08:00 | 13/Feb/2026 | 17:00 | PLANNED |  | RQ30562 | SD deferred
62 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 12/Feb/2026 | 7:00 | 12/Feb/2026 | 16:00 | PLANNED |  | RQ30542 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
63 | OCC_234 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 12/Feb/2026 | 7:00 | 12/Feb/2026 | 16:00 | PLANNED |  | RQ30557 | SD deferred
64 | OCC_234 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 12/Feb/2026 | 08:00 | 12/Feb/2026 | 17:00 | PLANNED |  | RQ30561 | SD deferred
65 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 11/Feb/2026 | 7:00 | 11/Feb/2026 | 16:00 | PLANNED |  | RQ30541 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
66 | OCC_234 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/Feb/2026 | 08:00 | 11/Feb/2026 | 17:00 | PLANNED |  | RQ30555 | SD deferred
67 | OCC_234 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 11/Feb/2026 | 7:00 | 11/Feb/2026 | 16:00 | PLANNED |  | RQ30556 | SD deferred
68 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 28/Feb/2026 | 8:00 | 28/Feb/2026 | 16:00 | PLANNED |  | RQ30531 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
69 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 10/Feb/2026 | 7:00 | 10/Feb/2026 | 16:00 | PLANNED |  | RQ30540 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
70 | OCC_234 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 17:00 | PLANNED |  | RQ30554 | SD deferred
71 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 27/Feb/2026 | 8:00 | 27/Feb/2026 | 16:00 | PLANNED |  | RQ30530 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
72 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 09/Feb/2026 | 7:00 | 09/Feb/2026 | 16:00 | PLANNED |  | RQ30539 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
73 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 26/Feb/2026 | 8:00 | 26/Feb/2026 | 16:00 | PLANNED |  | RQ30529 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
74 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 08/Feb/2026 | 7:00 | 08/Feb/2026 | 16:00 | PLANNED |  | RQ30538 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
75 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 25/Feb/2026 | 8:00 | 25/Feb/2026 | 16:00 | PLANNED |  | RQ30528 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
76 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 07/Feb/2026 | 7:00 | 07/Feb/2026 | 16:00 | PLANNED |  | RQ30537 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
77 | OCC_234 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | C | For Replacment of CB Drive mechanism. | 06/Feb/2026 | 09:00 | 08/Feb/2026 | 17:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30513 | SD may be deffered due to unavailability of 132kV Wokha - Chiephobozou line
78 | OCC_234 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 06/Feb/2026 | 08:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30553 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
79 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 24/Feb/2026 | 8:00 | 24/Feb/2026 | 16:00 | PLANNED |  | RQ30527 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
80 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 06/Feb/2026 | 7:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30536 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
81 | OCC_234 | POWERGRID | 132KV-SILCHAR-HAILAKANDI-2 | D | TLA installation work between tower number 08 to 16 | 06/Feb/2026 | 7:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30551 | Shutdown may be availed subject to availability of 132KV-SILCHAR-HAILAKANDI-1
82 | OCC_234 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 05/Feb/2026 | 08:00 | 05/Feb/2026 | 16:00 | PLANNED |  | RQ30552 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
83 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 23/Feb/2026 | 8:00 | 23/Feb/2026 | 16:00 | PLANNED |  | RQ30526 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
84 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 05/Feb/2026 | 7:00 | 05/Feb/2026 | 16:00 | PLANNED |  | RQ30535 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
85 | OCC_234 | POWERGRID | 132KV-SILCHAR-HAILAKANDI-2 | D | TLA installation work between tower number 08 to 16 | 05/Feb/2026 | 08:00 | 05/Feb/2026 | 16:00 | PLANNED |  | RQ30550 | Shutdown may be availed subject to availability of 132kV Silchar - Hailakandi-1
86 | OCC_234 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 04/Feb/2026 | 08:00 | 04/Feb/2026 | 16:00 | PLANNED |  | RQ30549 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
87 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 22/Feb/2026 | 8:00 | 22/Feb/2026 | 16:00 | PLANNED |  | RQ30525 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
88 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 04/Feb/2026 | 7:00 | 04/Feb/2026 | 16:00 | PLANNED |  | RQ30534 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
89 | OCC_234 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 03/Feb/2026 | 08:00 | 03/Feb/2026 | 16:00 | PLANNED |  | RQ30548 | Sd may be availed subject to the availability of 220kV Balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
90 | OCC_234 | POWERGRID | 132KV-BADARPUR-KARIMGANJ (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 03/Feb/2026 | 08:00 | 03/Feb/2026 | 16:00 | PLANNED | Existing System Improvement Related Shut Down | RQ30512 | Shutdown may be availed subject to availability of 132kV Kumarghat - Karimganj
91 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 21/Feb/2026 | 8:00 | 21/Feb/2026 | 16:00 | PLANNED |  | RQ30524 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
92 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 03/Feb/2026 | 7:00 | 03/Feb/2026 | 16:00 | PLANNED |  | RQ30533 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
93 | OCC_234 | POWERGRID | 132KV-BADARPUR-JIRIBAM(PG)-1 | D | Cross arm Painting Works by Silchar TLM | 02/Feb/2026 | 7:00 | 02/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30511 | Shutdown may be availed
94 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 20/Feb/2026 | 8:00 | 20/Feb/2026 | 16:00 | PLANNED |  | RQ30523 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
95 | OCC_234 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 02/Feb/2026 | 7:00 | 02/Feb/2026 | 16:00 | PLANNED |  | RQ30532 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line.
96 | OCC_234 | POWERGRID | 132KV-MELRIAT-ZUANGTUI-1 | C | Reconductoring of Balance 1.56 km of 132kV Melriat(PG)-Zemabawk TL with HTLS Conductor against NERES-XVIII project | 07/Feb/2026 | 08:00 | 16/Feb/2026 | 16:00 | PLANNED | Contruction | RQ30510 | Proposed connection from SLDC Mizoram during the shutdown: i) 132kV Melriat(PG) – Shimui- Zuangtai(Old) – Zuangtai(New) – Saitul – Vankal- Khawzawl – Champai ii) 132kV Aizwal – Lungmual – Melriat(MZ) – Lunglei – Serchip – E.Lungduar Study Comments: SD may be availed subject to availability of 132kV 132kV Melriat – Shimuii D/C, 132kV Aizwal – Melriat(PG), 132kV Aizwal – Kumarghat and 132kV Aizwal – Kolasib lines. Combined loading of 132kV Melriat(PG) – Shimuii D/C to be maintained below 75 MW. Under n-1 contingency of 132kV Aizwal – Melriat(PG), low voltage issue may arise in Lunglei and Serchip area of Mizoram Power System NERPC approval on the necessary protection setting changes arising from the rearrangement of the 132 kV transmission line.
97 | OCC_234 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | D | INSTALLATION OF TLSA IN TRANSMISSION LINE | 19/Feb/2026 | 8:00 | 19/Feb/2026 | 16:00 | PLANNED |  | RQ30522 | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
98 | OCC_234 | NETCL | 400KV-PALATANA-SILCHAR-1 | D | Rectification of jumper. | 20/Feb/2026 | 11:00 | 20/Feb/2026 | 12:30 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30509 | SD may be availed subject to the availability of 400kV Palatana-Silchar 2, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
99 | OCC_234 | NETCL | 400KV-BONGAIGAON-BYRNIHAT (KILLING) | D | Rectification of Jumper, tightening/ replacement of loose/rusted hardware fittings N&B etc. | 18/Feb/2026 | 11:00 | 18/Feb/2026 | 13:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30508 | SD deferred
100 | OCC_234 | NETCL | 400KV-AZARA-SILCHAR | D | Rectification of jumper, tightening of loose hardware fittings N&B etc.of | 11/Feb/2026 | 11:00 | 11/Feb/2026 | 13:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30507 | SD deferred
101 | OCC_234 | AEGCL | AGIA - 132KV - BUS 1 | D | PREVENTIVE MAINTENANCE | 22/Feb/2026 | 06:00 | 22/Feb/2026 | 10:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30505 | SD may be availed subject to availability of 132kV Mawngap - Nongstoin - Nangalbibra link
102 | OCC_234 | AEGCL | AZARA - 220KV - BUS 1 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 20/Feb/2026 | 05:00 | 20/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30499 | S/D may be availed subject to availability of 220kV Sarusajai - Sonapur-Samaguri link and 220kV Sarusajai - Jawaharnagar - Samaguri link. Load in Capital area, Jawaharnagar, Sonapur areas of Assam Power System is to be restricted within 180 MW. One unit of Langpi generation is recommended during the shutdown period to improve voltage profile. If one unit of Langpi is in service, load may be increased to 230 MW.
103 | OCC_234 | AEGCL | AZARA - 220KV - BUS 2 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 20/Feb/2026 | 05:00 | 20/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30503
104 | OCC_234 | AEGCL | AZARA - 220KV - BUS 1 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 19/Feb/2026 | 05:00 | 19/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30498 | S/D may be availed subject to availability of 220kV Sarusajai - Sonapur-Samaguri link and 220kV Sarusajai - Jawaharnagar - Samaguri link. Load in Capital area, Jawaharnagar, Sonapur areas of Assam Power System is to be restricted within 180 MW. One unit of Langpi generation is recommended during the shutdown period to improve voltage profile. If one unit of Langpi is in service, load may be increased to 230 MW.
105 | OCC_234 | AEGCL | AZARA - 220KV - BUS 2 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 19/Feb/2026 | 05:00 | 19/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30502
106 | OCC_234 | AEGCL | AZARA - 220KV - BUS 1 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 18/Feb/2026 | 05:00 | 18/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30497 | S/D may be availed subject to availability of 220kV Sarusajai - Sonapur-Samaguri link and 220kV Sarusajai - Jawaharnagar - Samaguri link. Load in Capital area, Jawaharnagar, Sonapur areas of Assam Power System is to be restricted within 180 MW. One unit of Langpi generation is recommended during the shutdown period to improve voltage profile. If one unit of Langpi is in service, load may be increased to 230 MW.
107 | OCC_234 | AEGCL | AZARA - 220KV - BUS 2 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 18/Feb/2026 | 05:00 | 18/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30501
108 | OCC_234 | AEGCL | AZARA - 220KV - BUS 1 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 17/Feb/2026 | 05:00 | 17/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30496 | S/D may be availed subject to availability of 220kV Sarusajai - Sonapur-Samaguri link and 220kV Sarusajai - Jawaharnagar - Samaguri link. Load in Capital area, Jawaharnagar, Sonapur areas of Assam Power System is to be restricted within 180 MW. One unit of Langpi generation is recommended during the shutdown period to improve voltage profile. If one unit of Langpi is in service, load may be increased to 230 MW.
109 | OCC_234 | AEGCL | AZARA - 220KV - BUS 2 | D | ALIGNMENT, TIGHETNING AND ADJUSTMENT OF ALL 220kV BUS ISOLATOR | 17/Feb/2026 | 05:00 | 17/Feb/2026 | 09:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30500
110 | OCC_234 | AEGCL | PAILAPPOL - 132KV - BUS 1 | D | PREVENTIVE MAINTENANCE (MAIN BUS) | 01/Feb/2026 | 06:00 | 01/Feb/2026 | 10:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30504 | Shutdown may be availed
111 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 27/Feb/2026 | 09:00 | 27/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30460 | SD may be availed subject to availability of 220kV BTPS(As) - Rangia I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia DC to be kept in enabled condtion
112 | OCC_234 | AEGCL | 220KV-AGIA-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 27/Feb/2026 | 09:00 | 27/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30484 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
113 | OCC_234 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING LOC 81-112 | 26/Feb/2026 | 10:00 | 26/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30451 | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
114 | OCC_234 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 240 TO 314 | 26/Feb/2026 | 08:00 | 26/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30463 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
115 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 25/Feb/2026 | 08:00 | 25/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30470 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
116 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 202 | 25/Feb/2026 | 08:00 | 25/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30493 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
117 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 24/Feb/2026 | 09:00 | 24/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30457 | SD may be availed subject to availability of 220kV BTPS(As) - Rangia II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia DC to be kept in enabled condtion
118 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 23/Feb/2026 | 08:00 | 23/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30447 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
119 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 24/Feb/2026 | 08:00 | 24/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30467 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
120 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 202 | 24/Feb/2026 | 08:00 | 24/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30492 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
121 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 23/Feb/2026 | 08:00 | 23/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30446 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
122 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 202 | 23/Feb/2026 | 08:00 | 23/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30491 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
123 | OCC_234 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 144 | 21/Feb/2026 | 08:00 | 21/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30488 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
124 | OCC_234 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | CORRIDOR CLEANING | 21/Feb/2026 | 06:00 | 21/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30442 | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
125 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 20/Feb/2026 | 09:00 | 20/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30459 | Sd may be availed subject to availability of 220kV BTPS - Rangia ckt-1 and 132kV Rangia - Motanga line. SPS related to tripping of 220kV BTPS - Rangia DC to be kept in enabled condition.
126 | OCC_234 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | CT INSTALLATION AT JIRIBAM FEEDER | 20/Feb/2026 | 09:00 | 20/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30476 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
127 | OCC_234 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 143 | 20/Feb/2026 | 08:00 | 20/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30487 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
128 | OCC_234 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 161 TO 25 | 19/Feb/2026 | 08:00 | 19/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30486 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
129 | OCC_234 | AEGCL | 220KV-AGIA-BTPS-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 18/Feb/2026 | 09:00 | 18/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30480 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. Under N-1 contingency involving the Agia–BTPS-1 line, the combined loading on the 400/220 kV ICTs at Azara reaches approximately 470 MW, resulting in a violation of N-1 compliance at Azara. To mitigate , the combined loading on Azara ICTs should be restricted to below 380 MW under such conditions.
130 | OCC_234 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEANING LOC 01-45 | 17/Feb/2026 | 10:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30450 | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
131 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 17/Feb/2026 | 09:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30456 | Sd may be availed subject to availability of 220kV BTPS - Rangia ckt-2 and 132kV Rangia - Motanga line. SPS related to tripping of 220kV BTPS - Rangia DC to be kept in enabled condition.
132 | OCC_234 | AEGCL | 220KV-AGIA-BTPS-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 17/Feb/2026 | 09:00 | 17/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30478 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line (which line loading to be maintained below 500A, 190MW). 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. Under N-1 contingency involving the Agia–BTPS-2 line, the combined loading on the 400/220 kV ICTs at Azara reaches approximately 470 MW, resulting in a violation of N-1 compliance at Azara. To mitigate , the combined loading on Azara ICTs should be restricted to below 380 MW under such conditions.
133 | OCC_234 | AEGCL | 132KV-HAFLONG-HAFLONG-1 | D | CORRIDOR CLEANING, JUNGLE CUTTING | 14/Feb/2026 | 06:00 | 14/Feb/2026 | 10:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30454 | SD may be availed.
134 | OCC_234 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 13/Feb/2026 | 09:00 | 13/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30448 | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
135 | OCC_234 | AEGCL | 132KV-GOHPUR-PAVOI-2 | D | BAY EQUIPMENT ESTING | 13/Feb/2026 | 09:00 | 13/Feb/2026 | 17:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30453 | S/D may be availed
136 | OCC_234 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | CORRIDOR CLEANING, JUNGLE CUTTING | 13/Feb/2026 | 09:00 | 13/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30475 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
137 | OCC_234 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING LOC 60-82 | 12/Feb/2026 | 10:00 | 12/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30495 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
138 | OCC_234 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 11/Feb/2026 | 09:00 | 11/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30474 | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
139 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 11/Feb/2026 | 08:00 | 11/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30469 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
140 | OCC_234 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 10/Feb/2026 | 09:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30449 | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
141 | OCC_234 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 240 TO 313 | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30462 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
142 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30466 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
143 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 202 | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30490 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
144 | OCC_234 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | LINE MAINTENANCE & DOUBLE JUMPERING & CORRIDOR CLEANING LOC 1 TO 202 | 09/Feb/2026 | 08:00 | 09/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30489 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
145 | OCC_234 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 81 TO 158 | 07/Feb/2026 | 09:30 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30443 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
146 | OCC_234 | AEGCL | 132KV-GOHPUR-PAVOI-1 | D | BAY EQUIPMENT ESTING | 07/Feb/2026 | 08:00 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30452 | SD may be availed Subject to availability of 132kV BNC(PG) -Gohpur, 132kV Gohpur- Nirjuli and 132kV Gohpur - Itanagar
147 | OCC_234 | AEGCL | 220KV-AGIA-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Feb/2026 | 09:00 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30483 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
148 | OCC_234 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Feb/2026 | 09:00 | 07/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30461 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
149 | OCC_234 | AEGCL | 220KV-AGIA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Feb/2026 | 09:00 | 06/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30481 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
150 | OCC_234 | AEGCL | 220KV-AGIA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Feb/2026 | 09:00 | 06/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30482 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
151 | OCC_234 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Feb/2026 | 08:00 | 06/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30445 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
152 | OCC_234 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 161 TO 24 | 06/Feb/2026 | 08:00 | 06/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30485 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
153 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | DOUBLE JUMPERING IN LOC 126, 128A, 129 | 05/Feb/2026 | 09:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30458 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
154 | OCC_234 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/Feb/2026 | 09:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30464 | SD May be availed subject to availability of 132 kV Panchgram - Lumshnong, 132 kV Panchgram - Badarpur.
155 | OCC_234 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 05/Feb/2026 | 09:00 | 05/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30473 | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
156 | OCC_234 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING LOC 31-59 | 04/Feb/2026 | 10:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30494 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
157 | OCC_234 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | DOUBLE JUMPERING AT LOC 126,128A,129 | 04/Feb/2026 | 09:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30455 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
158 | OCC_234 | AEGCL | 220KV-AGIA-BTPS-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Feb/2026 | 09:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30479 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
159 | OCC_234 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Feb/2026 | 08:00 | 04/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30444 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
160 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE | 04/Feb/2026 | 08:00 | 04/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30468 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
161 | OCC_234 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Feb/2026 | 09:00 | 03/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30471 | S/D may be availed.132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. The availability of generation from Leshka will support real-time grid operation during shutdown period. Consented from Assam.
162 | OCC_234 | AEGCL | 220KV-AGIA-BTPS-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Feb/2026 | 09:00 | 03/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30477 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
163 | OCC_234 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE | 03/Feb/2026 | 08:00 | 03/Feb/2026 | 15:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30465 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
164 | OCC_234 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 21/Feb/2026 | 09:30 | 21/Feb/2026 | 16:00 | PLANNED | R&U works Related Shut Down under PSDF | RQ30472 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
165 | OCC_234 | NEEPCO | AGTCCPP - GTG 2 | C | Generator Stator Rewinding Works | 02/Feb/2026 | 00:00 | 18/Mar/2026 | 23:59 | PLANNED | Existing System Improvement Related Shut Down | RQ30420 | SD may be availed. Consent from Beneficiaries is required.
166 | OCC_234 | NEEPCO | MONARCHAK(THERMAL) - GTG 1 | C | Shutdown taken by ONGC due to Pipeline Pigging works and gas well maintenance works | 10/Feb/2026 | 00:00 | 23/Feb/2026 | 23:59 | PLANNED |  | RQ30418 | SD may be availed after return of Palatana Generation Consent from Tripura
167 | OCC_234 | NEEPCO | MONARCHAK(THERMAL) - UNIT 2 | C | Shutdown taken by ONGC due to Pipeline Pigging works and gas well maintenance works | 10/Feb/2026 | 00:00 | 23/Feb/2026 | 23:59 | PLANNED |  | RQ30419 | SD may be availed after return of Palatana Generation Consent from Tripura
168 | OCC_234 | INDIGRID | MAIN BAY (102) OF 132KV-SURAJMANINAGAR (STERLITE)-BUDHJANGNAGAR-1 @SURAJMANINAGAR (STERLITE) - 132KV | D | For AMP work | 18/Feb/2026 | 08:00 | 18/Feb/2026 | 13:00 | PLANNED |  | RQ30417 | SD may be availed subject to no outage of elemnets.
169 | OCC_234 | INDIGRID | 132KV-SURAJMANINAGAR (STERLITE)-SURAJMANI NAGAR-1 | D | For AMP work | 17/Feb/2026 | 6:00 | 17/Feb/2026 | 11:00 | PLANNED |  | RQ30416 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) - Budhjungnagar line and 132kV PK bari(ISTS) - PK Bari
170 | OCC_234 | INDIGRID | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | For AMP work | 12/Feb/2026 | 08:00 | 12/Feb/2026 | 13:00 | PLANNED |  | RQ30415 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
171 | OCC_234 | INDIGRID | 132KV-PK BARI (STERLITE)-AMBASA-1 | D | For AMP work | 11/Feb/2026 | 08:00 | 11/Feb/2026 | 13:00 | PLANNED |  | RQ30414 | S/D may be availed subject to availability of 132kV Kamalpur-Ambassa link and Budhjunnagar-Jirania-Baramura-Gamaitilla-Ambassa link has to be present.
172 | OCC_234 | INDIGRID | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | For AMP work | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 12:00 | PLANNED |  | RQ30413 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
173 | OCC_234 | INDIGRID | BUS COUPLER BAY (104) OF SURAJMANINAGAR (STERLITE) - 132KV - BUS 1 AND SURAJMANINAGAR (STERLITE) - 132KV - BUS 2 @SURAJMANINAGAR (STERLITE) - 132KV | D | For AMP work | 17/Feb/2026 | 11:00 | 17/Feb/2026 | 16:00 | PLANNED |  | RQ30412 | SD may be availed subject to no outage of elements.
174 | OCC_234 | INDIGRID | MAIN BAY (412) OF 315 MVA 400KV/132KV ICT-2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 16/Feb/2026 | 11:00 | 16/Feb/2026 | 16:00 | PLANNED |  | RQ30411 | SD may be availed subject to availability of 400kV Palatana - SM Nagar 2 main bay and 400kV Palatana - SM Nagar and 400/132kV ICT-2 tie bay at 400 kV SM Nagar S/S
175 | OCC_234 | INDIGRID | TIE BAY (411) OF 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-2 AND 400KV/132KV SURAJMANINAGAR (STERLITE)-ICT-2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 16/Feb/2026 | 6:00 | 16/Feb/2026 | 11:00 | PLANNED |  | RQ30410 | SD may be availed subject to availability of 400kV Palatana - SM Nagar main bay and 400/132kV ICT-2 main bay at 400 kV SM Nagar S/S
176 | OCC_234 | INDIGRID | MAIN BAY (410) OF 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 15/Feb/2026 | 11:00 | 15/Feb/2026 | 16:00 | PLANNED |  | RQ30409 | SD may be availed subject to availability of 400/132kV ICT-2 main bay and 400kV Palatana - SM Nagar and 400/132kV ICT-2 tie bay at 400 kV SM Nagar S/S
177 | OCC_234 | INDIGRID | MAIN BAY (409) OF 400KV/132KV ICT-1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 15/Feb/2026 | 6:00 | 15/Feb/2026 | 11:00 | PLANNED |  | RQ30408 | SD may be availed subject to no outage of element
178 | OCC_234 | INDIGRID | TIE BAY (408) OF 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 AND 400KV/132KV SURAJMANINAGAR (STERLITE)-ICT-1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 14/Feb/2026 | 11:00 | 14/Feb/2026 | 16:00 | PLANNED |  | RQ30407 | SD may be availed subject to availability of 400kV Palatana - SM Nagar 1 main bay and 400/132kV ICT-1 main bay at 400 kV SM Nagar S/S
179 | OCC_234 | INDIGRID | MAIN BAY (407) OF 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 14/Feb/2026 | 6:00 | 14/Feb/2026 | 11:00 | PLANNED |  | RQ30406 | SD may be availed subject to availability of 400/132kV ICT-1 main bay and 400kV Palatana - SM Nagar and 400/132kV ICT-1 tie bay at 400 kV SM Nagar S/S
180 | OCC_234 | INDIGRID | MAIN BAY (406) OF SURAJMANINAGAR (STERLITE) - 420KV 125MVAR B/R 2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 13/Feb/2026 | 11:00 | 13/Feb/2026 | 16:00 | PLANNED |  | RQ30405 | SD may be availed subject to availability of 400kV SM Nagar - PK Bari 1 main bay and 125 MVAR BR2 & 400kV SM Nagar - PK Bari 1 tie bay at 400kV PK bari
181 | OCC_234 | INDIGRID | TIE BAY (405) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 AND SURAJMANINAGAR (STERLITE) - 400KV B/R 2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 13/Feb/2026 | 6:00 | 13/Feb/2026 | 11:00 | PLANNED |  | RQ30404 | Sd may be availed subject to availability of 400kV SM Nagar - PK Bari 1 main bay and 125 MVAR BR2 main bay at 400kV SM Nagar S/S
182 | OCC_234 | INDIGRID | MAIN BAY (404) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-2 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 12/Feb/2026 | 11:00 | 12/Feb/2026 | 16:00 | PLANNED |  | RQ30403 | SD may be availed subject to availability of 400kV SM Nagar - PK Bari II & 125 MVAR BR1tie bay and 125 MVAR main bay at 400kV PK Bari S/S
183 | OCC_234 | INDIGRID | MAIN BAY (403) OF SURAJMANINAGAR (STERLITE) - 420KV 125MVAR B/R 1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 12/Feb/2026 | 6:00 | 12/Feb/2026 | 11:00 | PLANNED |  | RQ30402 | SD may be availed subject to availability of 400kV SM Nagar - PK Bari II & 125 MVAR BR1tie bay and 400kV SM Nagar - PK Bari I main bay at 400kV PK Bari S/S
184 | OCC_234 | INDIGRID | TIE BAY (402) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-2 AND SURAJMANINAGAR (STERLITE) - 400KV B/R 1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 11/Feb/2026 | 11:00 | 11/Feb/2026 | 16:00 | PLANNED |  | RQ30401 | S/D may be availed subject to 400kV Sm Nagar(ISTS) - PK Bari(ISTS) II main bay and 125 MVAR BR1 main bay at 400kV PK Bari
185 | OCC_234 | INDIGRID | MAIN BAY (401) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 @SURAJMANINAGAR (STERLITE) - 400KV | D | For AMP work | 10/Feb/2026 | 08:00 | 10/Feb/2026 | 13:00 | PLANNED |  | RQ30400 | S/D may be availed subject subject to availability of main bay of 125MVAR BR-1 main bay and tie bay.
186 | OCC_234 | INDIGRID | BUS COUPLER BAY (104) OF PK BARI (STERLITE) - 132KV - BUS 1 AND PK BARI (STERLITE) - 132KV - BUS 2 @PK BARI (STERLITE) - 132KV | D | For AMP work | 09/Feb/2026 | 08:00 | 09/Feb/2026 | 13:00 | PLANNED |  | RQ30399 | S/D may be availed subject to no outage of elements
187 | OCC_234 | INDIGRID | MAIN BAY (412) OF 400KV/132KV PK BARI (STERLITE)-ICT-2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 08/Feb/2026 | 11:00 | 08/Feb/2026 | 16:00 | PLANNED |  | RQ30398 | SD may be availed subject to availability of 400kV SM Nagar - PK Bari II & 400/132kV ICT-2 tie bay and 400kV 400kV SM Nagar - PK Bari II main bay at 400kV PK Bari S/S
188 | OCC_234 | INDIGRID | TIE BAY (411) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-2 AND 400KV/132KV PK BARI (STERLITE)-ICT-2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 08/Feb/2026 | 6:00 | 08/Feb/2026 | 11:00 | PLANNED |  | RQ30397 | SD may be availed subject to availability of 400/132kV ICT-2 main bay and 400kV 400kV SM Nagar - PK Bari II main bay at 400kV PK Bari S/S
189 | OCC_234 | INDIGRID | MAIN BAY (410) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 07/Feb/2026 | 11:00 | 07/Feb/2026 | 16:00 | PLANNED |  | RQ30396 | SD may be availed subject to availability of 400kV SM Nagar 2 & 400/132kV ICT-2 tie bay and 400/132kV ICT-2 main bay at 400kV PK Bari S/S
190 | OCC_234 | INDIGRID | MAIN BAY (409) OF 400KV/132KV 315 MVA PK BARI (STERLITE)-ICT-1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 07/Feb/2026 | 6:00 | 07/Feb/2026 | 11:00 | PLANNED |  | RQ30395 | SD may be availed subject to availability of 400/132kV Ict-1 & 400kV SM Nagar - PK Bari I tie bay and 400kV SM Nagar - PK Bari I main bay at 400kV PK bari S/S
191 | OCC_234 | INDIGRID | TIE BAY (408) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 AND 400KV/132KV PK BARI (STERLITE)-ICT-1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 06/Feb/2026 | 11:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30394 | S/D may be availed subject to availability of main bays of 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 AND 400KV/132KV PK BARI (STERLITE)-ICT-1 @PK BARI (STERLITE) - 400KV
192 | OCC_234 | INDIGRID | MAIN BAY (407) OF 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 06/Feb/2026 | 6:00 | 06/Feb/2026 | 11:00 | PLANNED |  | RQ30393 | SD May be availed
193 | OCC_234 | INDIGRID | MAIN BAY (406) OF PK BARI (STERLITE) - 420KV 125MVAR B/R 2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 05/Feb/2026 | 11:00 | 05/Feb/2026 | 18:00 | PLANNED |  | RQ30392 | SD May be availed subject to availability of corresponding tie bay
194 | OCC_234 | INDIGRID | TIE BAY (405) OF 400KV-SILCHAR-PK BARI (STERLITE)-1 AND PK BARI (STERLITE) - 400KV B/R 2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 05/Feb/2026 | 6:00 | 05/Feb/2026 | 13:00 | PLANNED |  | RQ30391 | SD May be availed
195 | OCC_234 | INDIGRID | MAIN BAY (404) OF 400KV-SILCHAR-PK BARI (STERLITE)-2 @PK BARI (STERLITE) - 400KV | D | For AMP work | 04/Feb/2026 | 11:00 | 04/Feb/2026 | 16:00 | PLANNED |  | RQ30390 | S/D may be availed subject to availability of 400KV-SILCHAR-PK BARI (STERLITE)-2 & 125 MVAR BR1 tie bay 125 MVAR main bay at 400kV PK Bari S/S
196 | OCC_234 | INDIGRID | MAIN BAY (403) OF PK BARI (STERLITE) - 420KV 125MVAR B/R 1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 04/Feb/2026 | 6:00 | 04/Feb/2026 | 11:00 | PLANNED |  | RQ30389 | SD may be availed subject to availability of 400kV PK Bari - Silchar 2 main bay and 125 MVAR BR1 & 400kV PK Bari - Silchar 2 tie bay at 40kV PK Bari S/S
197 | OCC_234 | INDIGRID | TIE BAY (402) OF 400KV-SILCHAR-PK BARI (STERLITE)-2 AND PK BARI (STERLITE) - 400KV B/R 1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 03/Feb/2026 | 11:00 | 03/Feb/2026 | 16:00 | PLANNED |  | RQ30388 | S/D may be availed subject to availability of main bays of 400kV Silchar-2 and 125 MVAR BR1 at 400kV PK Bari
198 | OCC_234 | INDIGRID | MAIN BAY (401) OF 400KV-SILCHAR-PK BARI (STERLITE)-1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 01/Feb/2026 | 00:00 | 01/Feb/2026 | 13:00 | PLANNED |  | RQ30387 | SD deferred as duplicated
199 | OCC_234 | INDIGRID | TIE BAY (402) OF 400KV-SILCHAR-PK BARI (STERLITE)-2 AND PK BARI (STERLITE) - 400KV B/R 1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 03/Feb/2026 | 13:00 | 03/Feb/2026 | 18:00 | PLANNED |  | RQ30386 | SD deferred as duplicated
200 | OCC_234 | INDIGRID | MAIN BAY (401) OF 400KV-SILCHAR-PK BARI (STERLITE)-1 @PK BARI (STERLITE) - 400KV | D | For AMP work | 03/Feb/2026 | 6:00 | 03/Feb/2026 | 11:00 | PLANNED |  | RQ30385 | S/D may be availed subject to availability of 400kV Silchar-1 and tie bay of Silchar -1 and 125 MVAR BR-2 at 400kV PK Bari
201 | OCC_234 | NTPC | 400KV-BGTPP-BONGAIGAON-2 | D | For PM 4-189B Isolator | 12/Feb/2026 | 7:00 | 12/Feb/2026 | 16:00 | Existing System Normal Maintenance Related Shut Down | RQ30375 |  | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon I and 400/220kV ICT1&2 at BGTPP. SPS related to generation restriction in case of tripping of 400kV BGTPP - Bongaigaon ckt 1 &2 to be kept in ON condition if all 3 units are in service.
202 | OCC_234 | NTPC | 400KV-BGTPP-BONGAIGAON-1 | D | For PM 4-289B Isolator | 11/Feb/2026 | 7:00 | 11/Feb/2026 | 16:00 | Existing System Normal Maintenance Related Shut Down | RQ30374 |  | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon II and 400/220kV ICT1&2 at BGTPP. SPS related to generation restriction in case of tripping of 400kV BGTPP - Bongaigaon ckt 1 &2 to be kept in ON condition if all 3 units are in service.
203 | OCC_234 | NTPC | 400KV-BGTPP-BONGAIGAON-2 | D | For PM 4-189A Isolator | 10/Feb/2026 | 7:00 | 10/Feb/2026 | 16:00 | Existing System Normal Maintenance Related Shut Down | RQ30373 |  | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon I and 400/220kV ICT1&2 at BGTPP. SPS related to generation restriction in case of tripping of 400kV BGTPP - Bongaigaon ckt 1 &2 to be kept in ON condition if all 3 units are in service.
204 | OCC_234 | NTPC | 400KV-BGTPP-BONGAIGAON-1 | D | For PM 4-289A Isolator | 09/Feb/2026 | 7:00 | 09/Feb/2026 | 16:00 | Existing System Normal Maintenance Related Shut Down | RQ30372 |  | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon II and 400/220kV ICT1&2 at BGTPP. SPS related to generation restriction in case of tripping of 400kV BGTPP - Bongaigaon ckt 1 &2 to be kept in ON condition if all 3 units are in service.
205 | OCC_234 | NTPC | BGTPP - 400KV - BUS 2 | D | For PM 4-189B,4-289B,4-1089B Isolators | 12/Feb/2026 | 7:00 | 12/Feb/2026 | 16:00 |  | RQ30371 |  | SD may be availed subject to availability of other bus
206 | OCC_234 | NTPC | BGTPP - 400KV - BUS 2 | D | For PM 4-189B,4-289B,4-1089B Isolators | 11/Feb/2026 | 7:00 | 11/Feb/2026 | 16:00 |  | RQ30370 |  | SD may be availed subject to availability of other bus
207 | OCC_234 | NTPC | BGTPP - 400KV - BUS 1 | D | For PM 4-189A,4-289A,4-1089A Isolators | 10/Feb/2026 | 7:00 | 10/Feb/2026 | 16:00 |  | RQ30369 |  | SD may be availed subject to availability of other bus
208 | OCC_234 | NTPC | BGTPP - 400KV - BUS 1 | D | For PM 4-189A,4-289A,4-1089A Isolators | 09/Feb/2026 | 7:00 | 09/Feb/2026 | 16:00 |  | RQ30368 |  | SD may be availed subject to availability of other bus
209 | OCC_234 | NTPC | 400 KV BONGAIGAON 1 BAY (401) AT BGTPP | D | For PM 4-189B & 4-1089B Isolator | 12/Feb/2026 | 7:00 | 12/Feb/2026 | 16:00 | Existing System Improvement Related Shut Down | RQ30366 |  | SD may be availed
210 | OCC_234 | NTPC | 400 KV BONGAIGAON 2 BAY (402) AT BGTPP | D | For PM 4-289B & 4-1089B Isolator | 11/Feb/2026 | 7:00 | 11/Feb/2026 | 16:00 | Existing System Improvement Related Shut Down | RQ30367 |  | SD may be availed
211 | OCC_234 | NTPC | 400 KV BONGAIGAON 1 BAY (401) AT BGTPP | D | For PM 4-189A & 4-1089A Isolator | 10/Feb/2026 | 7:00 | 10/Feb/2026 | 16:00 | Existing System Normal Maintenance Related Shut Down | RQ30364 |  | SD may be availed
212 | OCC_234 | NTPC | 400 KV BONGAIGAON 2 BAY (402) AT BGTPP | D | For PM 4-289A & 4-1089A Isolator | 09/Feb/2026 | 7:00 | 09/Feb/2026 | 16:00 | Existing System Improvement Related Shut Down | RQ30365 |  | SD may be availed
213 | OCC_234 | NTPC | BGTPP - UNIT 2 | C | Unit 2 Overhauling | 05/Feb/2026 | 00:00 | 11/Mar/2026 | 00:00 | Existing System Normal Maintenance Related Shut Down | RQ30363 |  | SD may be availed.
215 | OCC_234 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Dismantling and Replacement of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 06/Feb/2026 | 09:00 | 06/Feb/2026 | 14:00 | PLANNED |  | RQ30361 | Shutdown may be availed subject to availability of 132kV ICT-1 at Panyor
216 | OCC_234 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Dismantling and Replacement of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 05/Feb/2026 | 09:00 | 05/Feb/2026 | 14:00 | PLANNED |  | RQ30360 | SD May be availed subject to availability of 132/33kV ICT-2 at Panyor
217 | OCC_234 | MEPTCL | 132KV-KHLIEHRIAT(ME)-KHELIEHRIAT-2 | D | Regular maintenance work at PG end | 20/Feb/2026 | 10:00 | 20/Feb/2026 | 16:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30359 | SD may be availed subject to availability of 132kV Khleihriat - Khleihriat II, 132kV Badarpur - Panchgram - Lumshnong- Khliehriat link and 220kV Killing - Mawngap D/C
218 | OCC_234 | MEPTCL | KHLIEHRIAT(ME) - 132KV - BUS 1 | D | Maintenance of the BSI of Y-phase of 132kV Lumshnong Bus side & R-phase of PG line-II at MePTCL end. | 03/Feb/2026 | 10:00 | 03/Feb/2026 | 16:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30358 | S/D may be availed Subject to the availability of 132kV Badarpur -Panchgram-Lumshnong link, 220kV Killing-Mawngap D/C and 220/132kV ICTs at Mawngap, 132kV Killing-EPIP-1-Epip 2-Umtru, 132kV Killing-EPIP-1-Epip 2-newUmtru-Umtru-Umian III-Umiam I link, 132kv Umiam I - Umiam(loading to be mainated under 55 MW), 132kV Umiam I-Mawlai(loading to be maintained under 35 MW). Khandong -kopili-misa link needs to be present.
219 | OCC_234 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 2 | D | Preventive maintenance of 220kV BUS-2 Isolator of Bus Coupler (201 89B) and 201 CT | 05/Feb/2026 | 10:00 | 05/Feb/2026 | 16:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30357 | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
220 | OCC_234 | MEPTCL | BYRNIHAT (KILLING) - 220KV - BUS 1 | D | Preventive maintenance of 220kV BUS-1 Isolator of Bus Coupler (201 89A) and 201 CB | 04/Feb/2026 | 10:00 | 04/Feb/2026 | 16:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30356 | Sd may be availed subject to the availability of other 220kV BUS, Khleiriat-Khleiriat-Mustem-Nehu-Umiam-Umtru-EPIP link, Khleiriat-Neighrims-Nehu-Mawlai-Mawngap link. Total Generation from Umian I, Umiam II, Umiam III and Umiam 4 , New Umtru must be atleast 20 MW.
221 | OCC_234 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 06/Feb/2026 | 09:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30355 | Shutdown may be availed
222 | OCC_234 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 05/Feb/2026 | 09:00 | 05/Feb/2026 | 16:00 | PLANNED |  | RQ30354 | S/D may be availed
223 | OCC_234 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 04/Feb/2026 | 09:00 | 04/Feb/2026 | 16:00 | PLANNED |  | RQ30353 | S/D may be availed
224 | OCC_234 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 03/Feb/2026 | 09:00 | 03/Feb/2026 | 16:00 | PLANNED |  | RQ30352 | S/D may be availed
225 | OCC_234 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-1 | C | Shutdown required for reconductoring of Brahmaputra River Crossing | 03/Feb/2026 | 09:00 | 06/Feb/2026 | 16:00 | PLANNED |  | RQ30351 | S/D may be availed
226 | OCC_234 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | D | Monthly changeover of 3x105MVA transformer (R,Y&B phases ICTs will be cgarged) | 05/Feb/2026 | 11:30 | 05/Feb/2026 | 13:00 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30350 | SD may be availed subject to the Imphal-Yurembam-Yiangangpopki-KongbaThubal-kakching-Churachandpur-Ningthoukhong link.
227 | OCC_234 | NEEPCO | KAMENG HEP - UNIT 3 | C | Continuous shutdown for Penstock-2 inspection, U-3 MIV works and APM | 01/Feb/2026 | 00:00 | 02/Mar/2026 | 23:59 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30348 | SD may be availed.
228 | OCC_234 | NEEPCO | KAMENG HEP - UNIT 4 | C | Continuous shutdown for Penstock-2 inspection and APM | 01/Feb/2026 | 00:00 | 02/Mar/2026 | 23:59 | PLANNED | Existing System Normal Maintenance Related Shut Down | RQ30349 | SD may be availed.
229 | OCC_234 | NEEPCO | PARE - UNIT 2 | C | APM of Unit-2 & Upgradation of Thyne-5 controller to Hipase controller to facilitate periodic testing of PHPS Unit-2 | 07/Feb/2026 | 00:00 | 26/Feb/2026 | 23:59 | PLANNED | Existing System Improvement Related Shut Down | RQ30347 | SD may be availed.