## Sheet1
Sl. no | OCC number | Name of requesting agency | Element name | Owner | Daily/ Continous | Reason | Shutdown start date | Shutdown start time | Shutdown end date | Shutdown end time | Requester remarks | Tag | Reference number | Study comments
1 | OCC_235 | KMTL | 400KV/220KV NEW KOHIMA-ICT-2 | KMTL | D | AMP Shutdown & Spare ICT Chang over | 23/Mar/2026 | 07:00 | 23/Mar/2026 | 19:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31061 | SD may be availed
2 | OCC_235 | KMTL | 400KV/220KV NEW KOHIMA-ICT-1 | KMTL | D | AMP Shutdown | 30/Mar/2026 | 07:00 | 30/Mar/2026 | 19:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31060 | SD may be availed
3 | OCC_235 | KMTL | NEW KOHIMA - 400KV B/R 2 | KMTL | C | AMP Shutdown | 19/Mar/2026 | 08:00 | 19/Mar/2026 | 08:00 | Bay 405 Isolator Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31059 | SD may be availed.
4 | OCC_235 | KMTL | NEW KOHIMA - 400KV B/R 1 | KMTL | D | AMP Shutdown | 20/Mar/2026 | 07:00 | 20/Mar/2026 | 15:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31058 | SD may be availed.
5 | OCC_235 | KMTL | 400KV-IMPHAL(PG)-NEW KOHIMA-2 | KMTL | D | AMP Shutdown | 24/Mar/2026 | 07:00 | 24/Mar/2026 | 15:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31057 | S/D may be availed subject to the availability of 400kV New Kohima 1 and 400kV Silchar - Imphal D/C. 125 MVAR BR at 400kV Imphal and one 125 MVAR BR 400kV New Kohima S/S to be kept open during the shutdown period
6 | OCC_235 | KMTL | 400KV-IMPHAL(PG)-NEW KOHIMA-1 | KMTL | D | AMP Shutdown | 25/Mar/2026 | 07:00 | 25/Mar/2026 | 14:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31054 | S/D may be availed subject to the availability of 400kV New Kohima 2 and 400kV Silchar - Imphal D/C. 125 MVAR BR at 400kV Imphal and one 125 MVAR BR 400kV New Kohima S/S to be kept open during the shutdown period
7 | OCC_235 | KMTL | 400KV-NEW KOHIMA-MARIANI (PG)-2 | KMTL | D | AMP Shutdown | 28/Mar/2026 | 07:00 | 28/Mar/2026 | 14:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31053 | SD may be availed subject to the availability of 400kV New Kohima - Mariani 1 and 400kV Silchar - Imphal D/C
8 | OCC_235 | KMTL | 400KV-NEW KOHIMA-MARIANI (PG)-1 | KMTL | D | AMP Shutdown | 27/Mar/2026 | 07:00 | 27/Mar/2026 | 14:00 | Maintenance Work | Existing System Normal Maintenance Related Shut Down | RQ31052 | SD may be availed subject to the availability of 400kV New Kohima - Mariani 2 and 400kV Silchar - Imphal D/C
9 | OCC_235 | NTPC | 400KV-BGTPP-BONGAIGAON-1 | POWERGRID | C | Bay 402 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | 05/Mar/2026 | 09:00 | 07/Mar/2026 | 18:00 | Bay 402 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | Existing System Normal Maintenance Related Shut Down | RQ31050 | Sd may be availed subject to availability of 400kV BGTPP - Bongaigaon II and 400/220kV ICT1&2 at BGTPP
10 | OCC_235 | NTPC | 400KV-BGTPP-BONGAIGAON-2 | POWERGRID | C | Bay 401 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | 02/Mar/2026 | 09:00 | 04/Mar/2026 | 18:00 | Bay 401 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | Existing System Normal Maintenance Related Shut Down | RQ31051 | Sd may be availed subject to availability of 400kV BGTPP - Bongaigaon I and 400/220kV ICT1&2 at BGTPP
11 | OCC_235 | NTPC | 400 KV BONGAIGAON 2 BAY (402) AT BGTPP | NTPC | C | Bay 402 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | 05/Mar/2026 | 09:00 | 07/Mar/2026 | 18:00 | Bay 402 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | Existing System Normal Maintenance Related Shut Down | RQ31049 | SD may be availed
12 | OCC_235 | NTPC | 400 KV BONGAIGAON 1 BAY (401) AT BGTPP | NTPC | C | Bay 401 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | 02/Mar/2026 | 09:00 | 04/Mar/2026 | 18:00 | Bay 401 PM, HDB alignment, CT Testing/ sampling , Breaker Testing | Existing System Normal Maintenance Related Shut Down | RQ31048 | SD may be availed
13 | OCC_235 | AEGCL | BALIPARA - 220KV - BUS 2 | POWERGRID | D | For replacement of rigid connectors of isolator 204-89A, 204-89B, 204-89T & 204-89L with 220kV Bus A & 220kV Bus B with flexible connector along with the allignment. | 07/Mar/2026 | 07:00 | 07/Mar/2026 | 16:00 | agm depota | R&U works Related Shut Down under PSDF | RQ31036 | SD may be availed subject to no ouatge of elements. All elements may be shifted to other bus prior to shutdown.
14 | OCC_235 | AEGCL | BALIPARA - 220KV - BUS 1 | POWERGRID | D | For replacement of rigid connectors of isolator 204-89A, 204-89B, 204-89T & 204-89L with 220kV Bus A & 220kV Bus B with flexible connector along with the allignment. | 06/Mar/2026 | 07:00 | 06/Mar/2026 | 16:00 | agm depota | R&U works Related Shut Down under PSDF | RQ31035 | SD may be availed subject to no ouatge of elements. All elements may be shifted to other bus prior to shutdown.
15 | OCC_235 | AEGCL | 220KV/132KV AGIA-ICT-2 | MEPTCL | D | ROUTINE TESTING (160MVA) | 12/Mar/2026 | 09:00 | 12/Mar/2026 | 16:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | RQ31032 | SD may be availed subject to availabity of Ict-1 & Ict-3 at Agia
16 | OCC_235 | AEGCL | 220KV/132KV AGIA-ICT-3 | AEGCL | D | ROUTINE TESTING (100MVA) | 07/Mar/2026 | 09:00 | 07/Mar/2026 | 16:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | RQ31034 | Sd may be availed subject to availability of 220/132kV ICT-1 &2 at Agia S/S
17 | OCC_235 | AEGCL | 220KV/132KV AGIA-ICT-1 | AEGCL | D | ROUTINE TESTING (100MVA) | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 16:00 | AGM T&T GOALPARA | R&U works Related Shut Down under PSDF | RQ31033 | Sd may be availed subject to availability of 220/132kV ICT-2 & 3 at Agia S/S
18 | OCC_235 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 17/Mar/2026 | 09:30 | 17/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ31027 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Atripura
19 | OCC_235 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & ROUTINE TESTING | 27/Mar/2026 | 09:00 | 27/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31012 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
20 | OCC_235 | AEGCL | 220KV-TINSUKIA-NRPP-1 | ASSAM | D | CORRIDOR CLEANING, LOC 95 TO 126 | 26/Mar/2026 | 10:00 | 26/Mar/2026 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | RQ30986 | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
21 | OCC_235 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Mar/2026 | 09:30 | 03/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ31026 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar and 132 Hailakandi-Dullavcherra , Intimation to Tripura
22 | OCC_235 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 26/Mar/2026 | 09:00 | 26/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31011 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
23 | OCC_235 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 161 TO 240 | 26/Mar/2026 | 08:00 | 26/Mar/2026 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | RQ30994 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
24 | OCC_235 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING | 14/Mar/2026 | 10:00 | 14/Mar/2026 | 16:00 | RE LEDO | R&U works Related Shut Down under PSDF | RQ30975 | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
25 | OCC_235 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 42 TO 50 | 24/Mar/2026 | 08:30 | 24/Mar/2026 | 16:30 | AGM SSJI & AGM SAMAGURI | R&U works Related Shut Down under PSDF | RQ31018 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line & 220kV Mirza - Sarusajai D/C
26 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 24/Mar/2026 | 08:00 | 24/Mar/2026 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | RQ30982 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
27 | OCC_235 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE AT LOC 176-249 AND 51-100 | 24/Mar/2026 | 08:00 | 24/Mar/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ30997 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
28 | OCC_235 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE AT LOC 42 TO 50 | 23/Mar/2026 | 08:30 | 23/Mar/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ30992 | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
29 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 23/Mar/2026 | 08:00 | 23/Mar/2026 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | RQ30981 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
30 | OCC_235 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | CORRIDOR CLEANING & JUNGLE CUTTING | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 16:00 | AGM T&T SILCHAR | R&U works Related Shut Down under PSDF | RQ31005 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
31 | OCC_235 | AEGCL | 220KV-TINSUKIA-NTPS-1 | ASSAM | D | CORRIDOR CLEANING, LOC 30 TO 67 | 19/Mar/2026 | 10:00 | 19/Mar/2026 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | RQ30985 | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
32 | OCC_235 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31009 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
33 | OCC_235 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31007 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
34 | OCC_235 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 143 | 17/Mar/2026 | 08:00 | 17/Mar/2026 | 16:00 | AGM NGAON T& T | R&U works Related Shut Down under PSDF | RQ31020 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
35 | OCC_235 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 143 | 16/Mar/2026 | 08:00 | 16/Mar/2026 | 16:00 | AGM NGAON T& T | R&U works Related Shut Down under PSDF | RQ31019 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
36 | OCC_235 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 13/Mar/2026 | 10:00 | 13/Mar/2026 | 13:00 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31016 | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link.
37 | OCC_235 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 12/Mar/2026 | 10:00 | 12/Mar/2026 | 13:00 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31015 | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link.
38 | OCC_235 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 12/Mar/2026 | 09:30 | 12/Mar/2026 | 16:00 | RE RUPAI & RE LEDO | R&U works Related Shut Down under PSDF | RQ30974 | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
39 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 16:00 | AGM MARIANI & AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31022 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
40 | OCC_235 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING | 11/Mar/2026 | 10:00 | 11/Mar/2026 | 16:00 | RE LEDO | R&U works Related Shut Down under PSDF | RQ30977 | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and 132kV Roing-Chapakhow-Rupai link
41 | OCC_235 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | AEGCL | D | CORRIDOR CLEANING, LOC 42 TO 82 | 11/Mar/2026 | 10:00 | 11/Mar/2026 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | RQ31029 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
42 | OCC_235 | AEGCL | 132KV-BISWANATH CHARIALI-GOHPUR-1 | INDIGRID | D | CORRIDOR CLEANING LOC 336 TO 361 | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | AGM DEPOTA | R&U works Related Shut Down under PSDF | RQ30973 | SD deferred as informed by Assam due to wrong punching of element.
43 | OCC_235 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | AEGCL | D | CORRIDOR CLEANING | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | RE GOLAGHAT | R&U works Related Shut Down under PSDF | RQ30984 | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
44 | OCC_235 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | RQ30990 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
45 | OCC_235 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | ROUTINE TESTING | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31010 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
46 | OCC_235 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 10/Mar/2026 | 09:30 | 10/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ31000 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
47 | OCC_235 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 10/Mar/2026 | 09:30 | 10/Mar/2026 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | RQ31001 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link
48 | OCC_235 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | AEGCL | D | CORRIDOR CLEANING & ROUTINE TESTING | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ30971 | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
49 | OCC_235 | AEGCL | 132KV-BISWANATH CHARIALI-GOHPUR-1 | INDIGRID | D | CORRIDOR CLEANING LOC 310 TO 335 | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | AGM DEPOTA | R&U works Related Shut Down under PSDF | RQ30972 | SD deferred as informed by Assam due to wrong punching of element.
50 | OCC_235 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | RE BOKAJAN | R&U works Related Shut Down under PSDF | RQ30983 | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
51 | OCC_235 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | RQ30988 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
52 | OCC_235 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 313 TO 240 | 10/Mar/2026 | 08:00 | 10/Mar/2026 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | RQ30993 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
53 | OCC_235 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 11/Mar/2026 | 09:30 | 11/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ30998 | S/D may be availed.132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. The availability of generation from Leshka will support real-time grid operation during shutdown period. Consented from Assam.
54 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 09/Mar/2026 | 08:00 | 09/Mar/2026 | 16:00 | AGM MARIANI & AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31021 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
55 | OCC_235 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING | 07/Mar/2026 | 10:00 | 07/Mar/2026 | 16:00 | RE LEDO | R&U works Related Shut Down under PSDF | RQ30976 | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and 132kV Roing-Chapakhow-Rupai link
56 | OCC_235 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Mar/2026 | 09:30 | 07/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ30991 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
57 | OCC_235 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 80 | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | RQ30978 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
58 | OCC_235 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 07/Mar/2026 | 09:00 | 07/Mar/2026 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | RQ30989 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
59 | OCC_235 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE AT LOC 229-235 | 09/Mar/2026 | 08:30 | 09/Mar/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31014 | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
60 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & DOUBLE JUMPERING AT LOC 1 TO 202 | 07/Mar/2026 | 08:00 | 07/Mar/2026 | 16:00 | AGM NGAON T& T | R&U works Related Shut Down under PSDF | RQ31025 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
61 | OCC_235 | AEGCL | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | For replacement of rigid connectors of isolator 204-89A, 204-89B, 204-89T & 204-89L with 220kV Bus A & 220kV Bus B with flexible connector along with the allignment | 07/Mar/2026 | 07:00 | 07/Mar/2026 | 16:00 | AGM DEPOTA | R&U works Related Shut Down under PSDF | RQ31031 | Sd may be availed subject to the availability of 220kV Balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
62 | OCC_235 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | AEGCL | D | CORRIDOR CLEANING, LOC 1 TO 41 | 06/Mar/2026 | 10:00 | 06/Mar/2026 | 16:00 | AGM TINSUKIA | R&U works Related Shut Down under PSDF | RQ31028 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
63 | OCC_235 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 16:00 | RE BOKAJAN | R&U works Related Shut Down under PSDF | RQ31003 | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
64 | OCC_235 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | CORRIDOR CLEANING & JUNGLE CUTTING | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 16:00 | AGM T&T SILCHAR | R&U works Related Shut Down under PSDF | RQ31004 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
65 | OCC_235 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | ROUTINE TESTING | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31008 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
66 | OCC_235 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | RQ30980 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
67 | OCC_235 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE AT LOC 101-175 AND 1-50 | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ30996 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
68 | OCC_235 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 313 TO 240 | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 16:00 | AGM SAMAGURI | R&U works Related Shut Down under PSDF | RQ31017 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
69 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & DOUBLE JUMPERING AT LOC 1 TO 202 | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 16:00 | AGM NGAON T& T | R&U works Related Shut Down under PSDF | RQ31024 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
70 | OCC_235 | AEGCL | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | For replacement of rigid connectors of isolator 204-89A, 204-89B, 204-89T & 204-89L with 220kV Bus A & 220kV Bus B with flexible connector along with the allignment | 06/Mar/2026 | 07:00 | 06/Mar/2026 | 16:00 | AGM DEPOTA | R&U works Related Shut Down under PSDF | RQ31030 | Sd may be availed subject to the availability of 220kV Balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
71 | OCC_235 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/Mar/2026 | 09:30 | 05/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ30995 | SD May be availed subject to availability of 132 kV Panchgram - Lumshnong & 132 kV Panchgram - Badarpur.
72 | OCC_235 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 16:00 | AGM RANGIA | R&U works Related Shut Down under PSDF | RQ30987 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
73 | OCC_235 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | AEGCL | D | CORRIDOR CLEANING | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 16:00 | RE GOLAGHAT | R&U works Related Shut Down under PSDF | RQ31002 | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
74 | OCC_235 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE AT LOC 283-284 | 05/Mar/2026 | 08:30 | 05/Mar/2026 | 16:30 | AGM SSJI & AGM GOALPARA | R&U works Related Shut Down under PSDF | RQ31013 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
75 | OCC_235 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & DOUBLE JUMPERING AT LOC 1 TO 202 | 05/Mar/2026 | 08:00 | 05/Mar/2026 | 16:00 | AGM NGAON T& T | R&U works Related Shut Down under PSDF | RQ31023 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
76 | OCC_235 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Mar/2026 | 09:30 | 04/Mar/2026 | 16:00 | AGM PANCHGRAM | R&U works Related Shut Down under PSDF | RQ30999 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
77 | OCC_235 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | ROUTINE TESTING | 04/Mar/2026 | 09:00 | 04/Mar/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31006 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
78 | OCC_235 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Mar/2026 | 08:00 | 04/Mar/2026 | 16:00 | AGM MARIANI | R&U works Related Shut Down under PSDF | RQ30979 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
79 | OCC_235 | POWERGRID | KUMARGHAT - 132KV B/R 1 | POWERGRID | C | For offline oil filtaration works | 30/Mar/2026 | 08:00 | 31/Mar/2026 | 23:59 |  | R&U works Related Shut Down under PSDF | RQ30970 | Shutdown may be availed
80 | OCC_235 | POWERGRID | SILCHAR - 400KV B/R 2 | POWERGRID | D | CSD Tuning works with operation | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30969 | SD may be availed
81 | OCC_235 | POWERGRID | FILTER BANK 1 SUB BANK 5 at BNC |  | D | AMP Works | 14/Mar/2026 | 09:00 | 14/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30968 | SD may be availed. NLDC consent is required.
82 | OCC_235 | POWERGRID | FILTER BANK 3 SUB BANK 2 at BNC |  | D | AMP Works | 07/Mar/2026 | 09:00 | 07/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30967 | SD may be availed. NLDC consent is required.
83 | OCC_235 | POWERGRID | FILTER BANK 3 SUB BANK 1 at BNC |  | D | AMP Works | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30966 | SD may be availed. NLDC consent is required.
84 | OCC_235 | POWERGRID | FILTER BANK 1 SUB BANK 3 at BNC |  | D | AMP Works | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30965 | SD may be availed. NLDC consent is required.
85 | OCC_235 | POWERGRID | FILTER BANK 2 SUB BANK 4 at BNC |  | D | AMP Works | 02/Mar/2026 | 09:00 | 02/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30964 | SD may be availed. NLDC consent is required.
86 | OCC_235 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-2 L/R@ BISWANATH CHARIALI - 400KV | POWERGRID | C | Instalaltion and commissioning of NGR Bypass Arrangement System (CT & CB erection and commissioning). Along with Main & Tie Bay. Same SD was proposed in the month of October-25 and same was not availed due to delay in Material receipt at site. | 26/Mar/2026 | 09:00 | 27/Mar/2026 | 17:00 |  | Contruction | RQ30958 | Shutdown may be availed
87 | OCC_235 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-1 L/R@ BISWANATH CHARIALI - 400KV | POWERGRID | C | Instalaltion and commissioning of NGR Bypass Arrangement System (CT & CB erection and commissioning). Along with Main & Tie Bay. Same SD was proposed in the month of October-25 and same was not availed due to delay in Material receipt at site. | 23/Mar/2026 | 09:00 | 24/Mar/2026 | 17:00 |  | Contruction | RQ30960 | Shutdown may be availed
88 | OCC_235 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 L/R@ BALIPARA - 400KV | POWERGRID | D | AMP works. Line Switching required for opening of the Reactor Isolator | 13/Mar/2026 | 09:00 | 13/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30963 | Sd may be availed
89 | OCC_235 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-3 L/R@ BISWANATH CHARIALI - 400KV | POWERGRID | D | Commissioning of NGR Bypass Arrangement System (CEA Approval received) | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 17:00 |  | Contruction | RQ30959 | SD may be availed. Around 3kV Voltage rise may be observed at Subansiri and BNC.
90 | OCC_235 | POWERGRID | 400KV-PALATANA-SILCHAR-2 L/R@ SILCHAR - 400KV | POWERGRID | D | CSD Tuning works with operation | 05/Mar/2026 | 08:00 | 05/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30962 | SD may be availed. 1-2kV Voltage rise may be observed at Silchar.
91 | OCC_235 | POWERGRID | 400KV-PALATANA-SILCHAR-1 L/R@ SILCHAR - 400KV | POWERGRID | D | CSD Tuning works with operation | 03/Mar/2026 | 08:00 | 03/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30961 | SD may be availed
92 | OCC_235 | POWERGRID | 400KV/132KV BISWANATH CHARIALI-ICT-1 | POWERGRID | C | Overhauling of OLTC drive , CB Drive mechanism and AMP works. | 16/Mar/2026 | 09:00 | 18/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30957 | SD may be availed subject to the availability of 400/132kV ICT-2 at BNC, 400V BNC- Panyor D/C line, 400/132kV ICT 1 & 2 at Panyor, 132kV Panyor-Pare, 132kV panyor-Lekhi and 132kV Panyor - Itangar lines.
93 | OCC_235 | POWERGRID | 220KV/132KV BALIPARA-ICT-2 | POWERGRID | D | AMP Works | 09/Mar/2026 | 09:00 | 09/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30955 | SD may be availed subject to availability of 220/132kV ICT-1 at Balipara S/S and 132kV Kameng-Khupi-Tenga-Balipara link
94 | OCC_235 | POWERGRID | 400KV/220KV MISA-ICT-1 | POWERGRID | D | Replacement of Electomechanical relay with Numerical Relay for LV OC /EF in ICT-3 with same settings at MISA Ss | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30954 | Sd may availed subject to availibility of 400/220kV ICT-2 &3 at Misa
95 | OCC_235 | POWERGRID | 132KV/33KV ROING-ICT-1 | POWERGRID | D | AMP Works | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30956 | SD may be availed subject to the availability of other ICT. Consented from AP
96 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 2 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 27/Mar/2026 | 09:00 | 27/Mar/2026 | 17:00 |  |  | RQ30949 | SD may be availed subject to no outage of elements
97 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 2 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 26/Mar/2026 | 09:00 | 26/Mar/2026 | 17:00 |  |  | RQ30948 | SD may be availed subject to no outage of elements
98 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 2 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 25/Mar/2026 | 09:00 | 25/Mar/2026 | 17:00 |  |  | RQ30947 | SD may be availed subject to no outage of elements
99 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 2 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 24/Mar/2026 | 09:00 | 24/Mar/2026 | 17:00 |  |  | RQ30946 | SD may be availed subject to no outage of elements
100 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 2 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 23/Mar/2026 | 09:00 | 23/Mar/2026 | 17:00 |  |  | RQ30945 | SD may be availed subject to no outage of elements
101 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 1 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 17:00 |  |  | RQ30944 | Sd may be availed subject to no outage of elements.
102 | OCC_235 | POWERGRID | IMPHAL(PG) - 400KV - BUS 2 | POWERGRID | D | Busbar Relay testing | 20/Mar/2026 | 08:00 | 20/Mar/2026 | 18:00 |  |  | RQ30953 | SD may be availed subject to no outage of elements. 132kV Imphal-Yerebam-Kongba-Thoubal-Kakching-Churachandpur-Ningthoukong link to be ensured.
103 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 1 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 19/Mar/2026 | 09:00 | 19/Mar/2026 | 17:00 |  |  | RQ30943 | Sd may be availed subject to no outage of elements.
104 | OCC_235 | POWERGRID | IMPHAL(PG) - 400KV - BUS 2 | POWERGRID | D | Busbar Relay testing | 19/Mar/2026 | 08:00 | 19/Mar/2026 | 18:00 |  |  | RQ30952 | SD may be availed subject to no outage of elements. 132kV Imphal-Yerebam-Kongba-Thoubal-Kakching-Churachandpur-Ningthoukong link to be ensured.
105 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 1 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 17:00 |  |  | RQ30942 | Sd may be availed subject to no outage of elements.
106 | OCC_235 | POWERGRID | IMPHAL(PG) - 400KV - BUS 1 | POWERGRID | D | Busbar Relay testing | 18/Mar/2026 | 08:00 | 18/Mar/2026 | 18:00 |  |  | RQ30951 | SD may be availed subject to no outage of elements. 132kV Imphal-Yerebam-Kongba-Thoubal-Kakching-Churachandpur-Ningthoukong link to be ensured.
107 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 1 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 17:00 |  |  | RQ30941 | Sd may be availed subject to no outage of elements.
108 | OCC_235 | POWERGRID | IMPHAL(PG) - 400KV - BUS 1 | POWERGRID | D | Busbar Relay testing | 17/Mar/2026 | 08:00 | 17/Mar/2026 | 18:00 |  |  | RQ30950 | SD may be availed subject to no outage of elements. 132kV Imphal-Yerebam-Kongba-Thoubal-Kakching-Churachandpur-Ningthoukong link to be ensured.
109 | OCC_235 | POWERGRID | SALAKATI - 220KV - BUS 1 | POWERGRID | D | Painting of rusted gantry tower members of 220 kV Main Bus-1. | 16/Mar/2026 | 09:00 | 16/Mar/2026 | 17:00 |  |  | RQ30940 | SD may be availed subject to no outage of elements. All the elements to be shift to Bus-2 before availing shutdown.
110 | OCC_235 | PENTL | 220KV-AGBPP GIS-NAMSAI GIS-2 | PENTL | C | Shifting of conductors from ERS Tower to Permanenet Towesr between location 08-09 due to theft of permanenet Tower members during erection of permanenet tower at location no.08. | 05/Mar/2026 | 08:00 | 06/Mar/2026 | 20:00 |  | Contruction | RQ30939 | Sd may availed subject to availibility of 220kV AGBPP - Namsai ckt-1, 132kV Panyor-Ziro-Daparijo-Along-Basar-Pasighat-Roing-Tesu-Namsai link. 45 MVAR BR at 220kV Namsai S/S need to be kept in off condtion duringthe shutdown period.
111 | OCC_235 | PENTL | 220KV-AGBPP GIS-NAMSAI GIS-1 | PENTL | C | Shifting of conductors from ERS Tower to Permanenet Towesr between location 08-09 due to theft of permanenet Tower members during erection of permanenet tower at location no.08. | 07/Mar/2026 | 08:00 | 08/Mar/2026 | 20:00 |  | Contruction | RQ30938 | Sd may availed subject to availibility of 220kV AGBPP - Namsai ckt-2, 132kV Panyor-Ziro-Daparijo-Along-Basar-Pasighat-Roing-Tesu-Namsai link. 45 MVAR BR at 220kV Namsai S/S need to be kept in off condtion duringthe shutdown period.
112 | OCC_235 | PENTL | 220KV-AGBPP GIS-NAMSAI GIS-1 | PENTL | D | Doube CKT SD required for day time due to the Diagonal strging in the exists ERS Tower for further faciliating Shifting of conductors from ERS Tower to Permanenet Towesr between location 08-09 due to theft of permanenet Tower members during erection of permanenet tower at location no.08. | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 17:00 |  | Contruction | RQ30937 | Sd may availed subject to availibility of 220kV AGBPP - Namsai ckt-2, 132kV Panyor-Ziro-Daparijo-Along-Basar-Pasighat-Roing-Tesu-Namsai link. 45 MVAR BR at 220kV Namsai S/S need to be kept in off condtion duringthe shutdown period.
113 | OCC_235 | POWERGRID | 400 KV, 315 MVA ICT 3 MAIN BAY AT SILCHAR | POWERGRID | D | AMP Works | 29/Mar/2026 | 08:00 | 29/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30932 | Sd may availed subject to availability of other main bay of ICT-3 at 400kV Silchar S?S
114 | OCC_235 | POWERGRID | 63 MVAR BUS REACTOR 2 BAY AT SILCHAR | POWERGRID | D | AMP Works | 28/Mar/2026 | 08:00 | 28/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30934 | SD may be availed subjected to availability of 400kV Silchar - Palatana 1 & 63 MVAR BR2 tie bay and 400kV Silchar - Palatana 1 main bay at 400kV Silchar S/S
115 | OCC_235 | POWERGRID | 400 KV BYRNIHAT BAY AT BONGAIGAON | POWERGRID | C | CB Mechanism overhauling works | 23/Mar/2026 | 09:00 | 26/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30920 | SD may be availed subject to availability of 400kV Bongaigaon - BGTPP I and 400kV Bongaigaon - Byrnihat tie bay and 400kV Bongaigaon - BGTPP I main bay at 400kV Bongaigaon S/S
116 | OCC_235 | POWERGRID | 132 KV, 160 MVA ICT 1 BAY AT BALIPARA | POWERGRID | D | AMP Works | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30936 | SD may be availed subject to availability of 220/132kV ICT-2 at Balipara S/S and 132kV Kameng-Khupi-Tenga-Balipara link
117 | OCC_235 | POWERGRID | TIE BAY () OF 400KV-BISWANATH CHARIALI-SUBANSIRI-3 AND 400KV-BISWANATH CHARIALI-SUBANSIRI-4 @BISWANATH CHARIALI - 400KV | POWERGRID | C | CB Mechanism overhauling works | 19/Mar/2026 | 09:00 | 21/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30935 | Sd may be availed subject to availability of 400KV-BISWANATH CHARIALI-SUBANSIRI-3 AND 400KV-BISWANATH CHARIALI-SUBANSIRI-4 and their corresponding main bay at 400kV BNC S/S
118 | OCC_235 | POWERGRID | 400 KV AZARA BAY AT BONGAIGAON | POWERGRID | C | CB Mechanism overhauling works | 18/Mar/2026 | 09:00 | 21/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30918 | SD may be availed subject to availability of 400kV Bongaigaon - Balipara III and 400kV Bongaigaon - Mirza tie bay and 400kV Bongaigaon - Balipara III main bay at 400kV Bongaigaon S/S
119 | OCC_235 | POWERGRID | 220 KV, 315 MVA ICT BAY AT BALIPARA | POWERGRID | D | AMP Works | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30931 | SD may be availed subject to availability of 315 MVA 220/132kV ICT-2, 220kV Misa-Samaguri D/C
120 | OCC_235 | POWERGRID | TIE BAY () OF 400KV-PALATANA-SILCHAR-1 AND SILCHAR - 400KV B/R 2 @SILCHAR - 400KV | POWERGRID | C | CB Mechanism overhauling works | 18/Mar/2026 | 09:00 | 21/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30933 | SD may be availed subject to availability of 400kV Palatan - Silchar I main bay and 400kV BR2 main bay at 400kV Silchar S/S
121 | OCC_235 | POWERGRID | BUS COUPLER BAY () OF HAFLONG - 132KV - BUS 1 AND HAFLONG - 132KV - BUS 2 @HAFLONG - 132KV | POWERGRID | D | AMP Works | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30919 | SD may be availed. 132kV Haloflong - Umrangshu and 132kV Halflong- Jiribam to be connected at same bus
122 | OCC_235 | POWERGRID | MAIN BAY () OF 400KV-BISWANATH CHARIALI-SUBANSIRI-3 @BISWANATH CHARIALI - 400KV | POWERGRID | C | Overhauling of CB Drive mechanism, CB Timing, DCRM, CRM & CT Tan Delta Test. | 29/Mar/2026 | 09:00 | 31/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30929 | Sd may be availed subject to availability of 400kV BNC-LS-3 & 400kV BNC-LS-4 tie bay and 400kV BNC - LS-4 main bay at 400kV BNC S/S
123 | OCC_235 | POWERGRID | MAIN BAY () OF 400KV-BISWANATH CHARIALI-BALIPARA-1 @BALIPARA - 400KV | POWERGRID | D | AMP Works | 16/Mar/2026 | 09:00 | 16/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30930 | Sd may be availed subject to availability of 400kV BNC - Baliapra III & 400kV Misa - Balaipara 1 tie bay and 400kV Misa - Balaipara 1 main bay at 400kV Balipara S/S
124 | OCC_235 | POWERGRID | BUS COUPLER BAY ( ) OF BISWANATH CHARIALI - 132KV - BUS 1 AND BISWANATH CHARIALI - 132KV - BUS 2 @BISWANATH CHARIALI - 132KV | POWERGRID | D | AMP Works | 13/Mar/2026 | 09:00 | 13/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30928 | SD may be availed
125 | OCC_235 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | POWERGRID | C | CB Mechanism overhauling works | 11/Mar/2026 | 09:00 | 14/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30921 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
126 | OCC_235 | POWERGRID | TIE BAY () OF 400KV-BISWANATH CHARIALI-SUBANSIRI-1 AND 400KV-BISWANATH CHARIALI-SUBANSIRI-2 @BISWANATH CHARIALI - 400KV | POWERGRID | C | CB Mechanism overhauling works | 09/Mar/2026 | 09:00 | 11/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30927 | SD may be availed subject to availability of main bays of 400KV-BNC-Subansiri 1 AND 400KV-BNC-Subansiri 2 @ 400kV BNC S/S
127 | OCC_235 | POWERGRID | MAIN (2) BAY OF 400KV-BALIPARA-MISA-1 @MISA - 400KV | POWERGRID | D | AMP Works | 16/Mar/2026 | 09:00 | 16/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30925 | SD may be availed subject to Misa-Balipara 2 and Balipara-Misa 1 to be charged to other bus via main bay.
128 | OCC_235 | POWERGRID | TIE BAY () OF BALIPARA - 400KV B/R 3 AND FUTURE @BALIPARA - 400KV | POWERGRID | D | AMP Works | 07/Mar/2026 | 09:00 | 07/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30926 | SD may be subject to no outage elements
129 | OCC_235 | POWERGRID | 400,50 MVAR BUS REACTOR 1 BAY AT BALIPARA | POWERGRID | D | AMP Works | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30924 | SD may be availed
130 | OCC_235 | POWERGRID | 400 KV BONGAIGAON 4 MAIN BAY(WITH 63 MVAR LINE REACTOR ) (422) AT BALIPARA | POWERGRID | D | AMP Works | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30923 | SD may be availed subject to the availability of 400kV Bongaigaon - Balipara 4 and 400kV Balipara - Kameng 1 tie bay and 400kV Balipara - Kameng 1 main bay at 400kV Balipara S/S
131 | OCC_235 | POWERGRID | 400 KV BONGAIGAON 3 MAIN BAY(WITH 63 MVAR LINE REACTOR ) (419) AT BALIPARA | POWERGRID | D | AMP Works | 02/Mar/2026 | 09:00 | 02/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30922 | SD may be availed subject to the availability of 400kV Bongaigaon - Balipara 3 and 400kV Balipara - Kameng 2 tie bay and 400kV Balipara - Kameng 2 main bay at 400kV Balipara S/S
132 | OCC_235 | POWERGRID | 132KV-BISWANATH CHARIALI-PAVOI-2 | POWERGRID | D | AMP of line equiments | 28/Mar/2026 | 08:00 | 28/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30896 | SD may be availed subjected to availability of 132kV BNC - Pavoi 1, 132kV BNC - Gohpur and 132kV Pavoi - Gohpur D/C
133 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 28/Mar/2026 | 08:00 | 28/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30897 | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-1 and 132kV Doyang - Mokokchung(NL) - Mokokchung(PG) link. Intimation to NEEPCO
134 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 27/Mar/2026 | 08:00 | 27/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30895 | SD may be availed subject to the availabitiy of 132kV Dimapur - Doyang 1 and 132kV Doyang - Mokokchung(NL) - Mokokchung(PG) link
135 | OCC_235 | POWERGRID | 220KV-MISA-SAMAGURI-2 | POWERGRID | D | AMP works of Bay equiments Misa and Samaguri end . | 26/Mar/2026 | 09:00 | 26/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30894 | S/D may be availed subject to availability of 220kV Misa - Samaguri-1 and 220kV Balipara - Sonabil D/C, 220kV Mirza - Sarusajai D/C and 220kV Samaguri - Mariani
136 | OCC_235 | POWERGRID | 220KV-MISA-SAMAGURI-1 | POWERGRID | D | AMP works of Bay equiments Misa and Samaguri end . | 24/Mar/2026 | 09:00 | 24/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30893 | S/D may be availed subject to availability of 220kV Misa - Samaguri-2 and 220kV Balipara - Sonabil D/C, 220kV Mirza - Sarusajai D/C and 220kV Samaguri - Mariani
137 | OCC_235 | POWERGRID | 132KV-MELRIAT-SINHMUI-2 | POWERGRID | D | AMP WORKS | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30891 | Sd may be availed subject to availability of 132kV Melriat - Shimuii I
138 | OCC_235 | POWERGRID | 132KV-DAPORIJU-ZIRO-1 | DOP,ARUNACHAL PRADESH | D | RETROFITMENT OF 86 RELAY AND RELAY TESTING WORKS IN DAPORIJO BAY. | 02/Mar/2026 | 08:00 | 02/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30892 | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
139 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 26/Mar/2026 | 08:00 | 26/Mar/2026 | 17:00 |  |  | RQ30917 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
140 | OCC_235 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 19/Mar/2026 | 08:00 | 19/Mar/2026 | 16:00 |  | Existing System Improvement Related Shut Down | RQ30890 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required. FTC procedure to be followed
141 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 25/Mar/2026 | 08:00 | 25/Mar/2026 | 17:00 |  |  | RQ30916 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
142 | OCC_235 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | POWERGRID | D | AMP WORKS | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30888 | SD may be availed subject to availability of 132kV Melriat - Simuii II
143 | OCC_235 | POWERGRID | 220KV-MISA-KOPILI-1 | POWERGRID | D | AMP WORKS | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30889 | SD may be availed subject to availability of 220kV Misa - Kopili II & III
144 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 24/Mar/2026 | 08:00 | 24/Mar/2026 | 17:00 |  |  | RQ30915 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
145 | OCC_235 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30887 | Sd may be availed subject to availability of 400kV Silachar - PK Bari I and 400 kV Palatana - SM Nagar - PK Bari link.
146 | OCC_235 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/Mar/2026 | 08:00 | 17/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30886 | Sd may be availed subject to availability of 400kV BNC - Balipara ckt II, III, IV
147 | OCC_235 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/Mar/2026 | 08:00 | 17/Mar/2026 | 17:00 |  |  | RQ30913 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
148 | OCC_235 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 23/Mar/2026 | 08:00 | 23/Mar/2026 | 17:00 |  |  | RQ30914 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
149 | OCC_235 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/Mar/2026 | 09:00 | 16/Mar/2026 | 17:00 |  | Existing System Improvement Related Shut Down | RQ30885 | Sd may be availed subject to availability of 400kV Silachar - PK Bari II and 400 kV Palatana - SM Nagar - PK Bari link.
150 | OCC_235 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/Mar/2026 | 08:00 | 16/Mar/2026 | 17:00 |  |  | RQ30912 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
151 | OCC_235 | POWERGRID | 132KV-HAFLONG-JIRIBAM-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 14/Mar/2026 | 08:00 | 14/Mar/2026 | 16:00 |  | Existing System Improvement Related Shut Down | RQ30884 | SD may be availed subjected to availability of 132kV Khandong - Umrangsho - Haflong (PG)
152 | OCC_235 | POWERGRID | 132KV-ROING-TEZU-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Tezu TLM | 25/Mar/2026 | 08:00 | 25/Mar/2026 | 17:00 |  |  | RQ30911 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
153 | OCC_235 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | AEGCL,POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/Mar/2026 | 08:00 | 13/Mar/2026 | 16:00 |  | Existing System Improvement Related Shut Down | RQ30883 | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
154 | OCC_235 | POWERGRID | 132KV-ROING-TEZU-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Tezu TLM | 24/Mar/2026 | 08:00 | 24/Mar/2026 | 17:00 |  |  | RQ30910 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
155 | OCC_235 | POWERGRID | 132KV-BISWANATH CHARIALI-PAVOI-1 | POWERGRID | D | AMP of line equiments | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30881 | SD may be availed subject to availability of 132kV BNC - Pavoi-2 and 132kV BNC - gohpur
156 | OCC_235 | POWERGRID | 132KV-HAFLONG-HAFLONG-1 | ASSAM | D | AMP works of line Terminal Equipments | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ30882 | SD may be availed.
157 | OCC_235 | POWERGRID | 132KV-ROING-TEZU-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Tezu TLM | 23/Mar/2026 | 08:00 | 23/Mar/2026 | 17:00 |  |  | RQ30909 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
158 | OCC_235 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/Mar/2026 | 08:00 | 11/Mar/2026 | 17:00 |  |  | RQ30906 | SD may be availed subject the availability of 400kV Balipara - Kameng 1
159 | OCC_235 | POWERGRID | 132KV-ROING-TEZU-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Tezu TLM | 2026-03-22 | 08:00 | 2026-03-22 | 17:00 |  |  | RQ30908 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
160 | OCC_235 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | AEGCL | D | AMP Works | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30880 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
161 | OCC_235 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Mar/2026 | 08:00 | 10/Mar/2026 | 17:00 |  |  | RQ30905 | SD may be availed subject to availability of 400kV Balipara - Kameng 1
162 | OCC_235 | POWERGRID | 132KV-ROING-TEZU-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Tezu TLM | 21/Mar/2026 | 08:00 | 21/Mar/2026 | 17:00 |  |  | RQ30907 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
163 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 17:00 |  |  | RQ30904 | SD may be availed subject to the availability of 400kV Balipara - Misa-1 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
164 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Mar/2026 | 09:00 | 09/Mar/2026 | 17:00 |  |  | RQ30903 | SD may be availed subject to the availability of 400kV Balipara - Misa-1 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
165 | OCC_235 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | POWERGRID | D | AMP Works | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ30898 | SD may be availed
166 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 17:00 |  |  | RQ30902 | SD may be availed subject to the availability of 400kV Balipara - Misa-1 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
167 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 04/Mar/2026 | 09:00 | 04/Mar/2026 | 17:00 |  |  | RQ30901 | SD may be availed subject to the availability of 400kV Balipara - Misa-2 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
168 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 17:00 |  |  | RQ30900 | SD may be availed subject to the availability of 400kV Balipara - Misa-2 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
169 | OCC_235 | POWERGRID | 400KV-BALIPARA-MISA-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 02/Mar/2026 | 09:00 | 02/Mar/2026 | 17:00 |  |  | RQ30899 | SD may be availed subject to the availability of 400kV Balipara - Misa-2 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period.
170 | OCC_235 | POWERGRID | 132KV-MELRIAT-ZUANGTUI-1 | POWERGRID | C | Reconductoring of Balance 1.56 km of 132kV Melriat(PG)-Zemabawk TL with HTLS Conductor against NERES-XVIII project | 01/Mar/2026 | 09:00 | 15/Mar/2026 | 17:00 |  | Contruction | RQ30879 | SD may bShutdown of 132kV Melriat(PG) – Zuangtai line on continuous basis: Proposed connection from SLDC Mizoram during the shutdown: i) 132kV Melriat(PG) – Shimui- Zuangtai(Old) – Zuangtai(New) – Saitul – Vankal- Khawzawl – Champai ii) 132kV Aizwal – Lungmual – Melriat(MZ) – Lunglei – Serchip – E.Lungduar Before charging of 132kV Shihmui- Zuangtui (old)line, NERPC approval for revised protection setting needs to be ensured by P&ED Mizoram. After charging of 132kV Shihmui- Zuangtui (old) line, The SD of 132kV Melriat-Zuangtui line may be availed as per study comments. Study Comments: SD may be availed subject to availability of 132kV 132kV Melriat – Shimuii D/C, 132kV Aizwal – Melriat(PG), 132kV Aizwal – Kumarghat and 132kV Aizwal – Kolasib lines. Combined loading of 132kV Melriat(PG) – Shimuii D/C to be maintained below 75 MW. Under n-1 contingency of 132kV Aizwal – Melriat(PG), low voltage issue may arise in Lunglei and Serchip area of Mizoram Power System NERPC approval is required for the necessary protection setting changes after reverting the rearrangement, once the SD of the 132 kV Melriat–Zuangtui line is returned.
171 | OCC_235 | INDIGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | POWERGRID | D | Insulator Replacement Work | 13/Mar/2026 | 08:00 | 13/Mar/2026 | 15:00 |  |  | RQ30877 | Sd may be availed subject to availability of 400kV Silachar - PK Bari I and 400 kV Palatana - SM Nagar - PK Bari link.
172 | OCC_235 | INDIGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | POWERGRID | D | Insulator Replacement Work | 11/Mar/2026 | 08:00 | 11/Mar/2026 | 15:00 |  |  | RQ30876 | Sd may be availed subject to availability of 400kV Palatana - SM Nagar-PK bari link and 400kV Silchar - PK Bari 2. One of the Bus Reactor to kept in off condition avoid low volatge in case of tripping of 400kV Palatana - SM Nagar under n-1 contingecy.
173 | OCC_235 | INDIGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-2 | ENICL | D | BLACK INSULATOR REPLACEMENT | 09/Mar/2026 | 08:00 | 09/Mar/2026 | 16:00 |  |  | RQ30875 | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
174 | OCC_235 | INDIGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | ENICL | D | INSULATOR REPLACEMENT | 05/Mar/2026 | 08:00 | 05/Mar/2026 | 15:00 |  |  | RQ30874 | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
175 | OCC_235 | INDIGRID | 400KV-BONGAIGAON-ALIPURDUAR-2 | ENICL | D | To rectify shutdown defect like Guard ring, C.C ring, Arcing horn, Jumper cone, Conductor string cut etc. related defect. | 31/Mar/2026 | 09:00 | 31/Mar/2026 | 17:00 |  |  | RQ30873 | SD may be availed subject to the availabitiy of 400kV Bongaigaon - Alipurduar 1 and 400kV Bongaigaon - New Siliguri D/C. NER-ER TTC/ATC to be revised
176 | OCC_235 | INDIGRID | 400KV-BONGAIGAON-ALIPURDUAR-1 | ENICL | D | To rectify shutdown defect like Guard ring, C.C ring, Arcing horn, Jumper cone, Conductor string cut etc. related defect. | 30/Mar/2026 | 09:00 | 30/Mar/2026 | 17:00 |  |  | RQ30872 | SD may be availed subject to the availabitiy of 400kV Bongaigaon - Alipurduar 2 and 400kV Bongaigaon - New Siliguri D/C. NER-ER TTC/ATC to be revised
177 | OCC_235 | INDIGRID | 400KV/132KV SURAJMANINAGAR (STERLITE)-ICT-2 | INDIGRID | D | Black insulator replacement and AMP | 12/Mar/2026 | 06:00 | 12/Mar/2026 | 16:00 |  |  | RQ30870 | SD may be availed SD may be availed subject the availability of 400/132kV ICT-1 at Sm nagar and 132kV Palatana - SM Nagar
178 | OCC_235 | INDIGRID | 400KV/132KV SURAJMANINAGAR (STERLITE)-ICT-1 | INDIGRID | D | Black insulator replacement and AMP | 10/Mar/2026 | 06:00 | 10/Mar/2026 | 16:00 |  |  | RQ30871 | SD may be availed subject to availability of 132kV Palatana - SM Nagar & 400/132kV ICT-2 at 400k SM Nagar S/S
179 | OCC_235 | INDIGRID | 400KV/132KV PK BARI (STERLITE)-ICT-2 | INDIGRID | D | Insulator Replacment Work | 09/Mar/2026 | 06:00 | 09/Mar/2026 | 16:00 |  |  | RQ30869 | SD may be availed subject to the availability 400/132kV ICT-1 at PK Bari
180 | OCC_235 | INDIGRID | 400KV/132KV PK BARI (STERLITE)-ICT-1 | INDIGRID | D | Insulator Replacement Work | 08/Mar/2026 | 06:00 | 08/Mar/2026 | 16:00 |  |  | RQ30868 | SD may be availed subject to the availability 400/132kV ICT-2 at PK Bari
181 | OCC_235 | INDIGRID | 400KV-SILCHAR-MISA-2 | INDIGRID | D | To rectify the shutdown defect rectification along with installation of bird reflector. | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 17:00 | Mass mobilization of manpower |  | RQ30867 | Sd may be availed subject to availability of 400kV Silchar - Misa I, 400kV Silchar - Killing and 400kV Silchar - Mirza
182 | OCC_235 | INDIGRID | 400KV-SILCHAR-MISA-1 | INDIGRID | D | To rectify shutdown defect rectification along with installation of bird reflector. | 16/Mar/2026 | 9:00 | 16/Mar/2026 | 17:00 | Mass mobilization of manpower |  | RQ30866 | Sd may be availed subject to availability of 400kV Silchar - Misa II, 400kV Silchar - Killing and 400kV Silchar - Mirza
183 | OCC_235 | INDIGRID | 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-2 | ENICL | D | to replace the insulators at SM Nagar & PK Bari SS, line outage is required | 07/Mar/2026 | 08:00 | 07/Mar/2026 | 15:00 |  |  | RQ30865 | SD may be availed subject to availability of 400kV Palatana - SM Nagar and 400kV SM Nagra - PK Bari ckt 1. One reactor to be remain in off condtion at 400kV SM Nagar to avoid low voltage issue in case of tripping of 400kV Palatana - SM Nagar under n-1 contingency.
184 | OCC_235 | INDIGRID | 400KV-SURAJMANINAGAR (STERLITE)-PK BARI (STERLITE)-1 | ENICL | D | To change the insulator at SM Nagar & PK Bari SS, SMPK CKT-1 shutdown is required. | 06/Mar/2026 | 08:00 | 06/Mar/2026 | 15:00 |  |  | RQ30864 | SD may be availed subject to availability of 400kV Palatana - SM Nagar and 400kV SM Nagra - PK Bari ckt 2. One reactor to be remain in off condtion at 400kV SM Nagar to avoid low voltage issue in case of tripping of 400kV Palatana - SM Nagar under n-1 contingency.
185 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV B/R 2 | INDIGRID | D | Insulator Replacement Work & AMP | 13/Mar/2026 | 08:00 | 13/Mar/2026 | 15:00 |  |  | RQ30863 | SD may be availed
186 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV B/R 1 | INDIGRID | D | Insulator Replacement Work | 11/Mar/2026 | 08:00 | 11/Mar/2026 | 15:00 |  |  | RQ30862 | Sd may be availed
187 | OCC_235 | INDIGRID | PK BARI (STERLITE) - 400KV B/R 2 | INDIGRID | D | Insulator Replacement | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 15:00 |  |  | RQ30861 | SD may be availed
188 | OCC_235 | INDIGRID | PK BARI (STERLITE) - 400KV B/R 1 | INDIGRID | D | INSULATOR REPLACEMENT | 10/Mar/2026 | 08:00 | 10/Mar/2026 | 15:00 |  |  | RQ30860 | Sd may be availed
189 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Black Insulator Replacement work & AMP | 13/Mar/2026 | 08:00 | 13/Mar/2026 | 16:00 |  |  | RQ30859 | SD may be availed subject to availability to no outage of elements except 400kV BR2 at SM Nagar
190 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Black Insulator Replacement work & AMP | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 16:00 |  |  | RQ30858 | SD may be availed subject to no outage of elements except 400/132kV ICT-2 at SM Nagar
191 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Black Insulator Replacement work & AMP | 11/Mar/2026 | 08:00 | 11/Mar/2026 | 16:00 |  |  | RQ30857 | Sd may be availed subject to no outage of elements except 400kV BR -1 at SM Nagar
192 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Black Insulator Replacement work & AMP | 10/Mar/2026 | 08:00 | 10/Mar/2026 | 16:00 |  |  | RQ30856 | SD may be availed subject to no outage of elements.
193 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Black Insulator Replacement work | 09/Mar/2026 | 08:00 | 09/Mar/2026 | 16:00 |  |  | RQ30855 | SD may be availed subject to no outage of elements.
194 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Black Insulator Replacement work | 08/Mar/2026 | 08:00 | 08/Mar/2026 | 16:00 |  |  | RQ30854 | SD may be availed subject to no outage of elements.
195 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Black Insulator Replacement work | 07/Mar/2026 | 08:00 | 07/Mar/2026 | 16:00 |  |  | RQ30853 | SD may be availed subject to no outage of elements other than 400kV SM Nagar - PK Bari2
196 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Insulator Replacement Work | 12/Mar/2026 | 08:00 | 12/Mar/2026 | 16:00 |  |  | RQ30852 | SD may be availed subject to no outage of elements except BR-2 at PK Bari
197 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Insulator Replacement Work | 10/Mar/2026 | 08:00 | 10/Mar/2026 | 16:00 |  |  | RQ30851 | SD may be availed subject to no outage of elements
198 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Insulator Replacement Work | 09/Mar/2026 | 08:00 | 09/Mar/2026 | 16:00 |  |  | RQ30850 | SD may be availed subject to no outage of elements except 400/132kV ICT-2 at PK Bari
199 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 2 | INDIGRID | D | Insulator Replacement Work | 08/Mar/2026 | 08:00 | 08/Mar/2026 | 16:00 |  |  | RQ30849 | SD may be availed subject to no outage of elements except 400/132kV ICT-1 at PK Bari
200 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Insulator Replacement Work | 13/Mar/2026 | 06:00 | 13/Mar/2026 | 16:00 |  |  | RQ30848 | SD may be availed subject to availability to no outage of elements except 400kV 400kV Silchar - PK Bari 2
201 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Insulator Replacement Work | 11/Mar/2026 | 06:00 | 11/Mar/2026 | 16:00 |  |  | RQ30847 | Sd may be availed subject to no outage of elements except 400kV Silchar - PK Bari 1 at 400kV Pk Bari S/S
202 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Insulator Replacement Work | 07/Mar/2026 | 06:00 | 07/Mar/2026 | 16:00 |  |  | RQ30846 | SD may be availed subject to no outage of elements other than 400kV SM Nagar - PK Bari2
203 | OCC_235 | INDIGRID | 400 KV PK BARI (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Insulator Replacement Work | 06/Mar/2026 | 06:00 | 06/Mar/2026 | 16:00 |  |  | RQ30845 | SD may be availed subject to no outage of elements other than 400kV SM Nagar - PK Bari1
204 | OCC_235 | INDIGRID | SURAJMANINAGAR (STERLITE) - 400KV - BUS 1 | INDIGRID | D | Busbar Insulator Replcement work | 06/Mar/2026 | 06:00 | 06/Mar/2026 | 16:00 |  |  | RQ30844 | SD may be availed subject to no outage of elements other than 400kV SM Nagar - PK Bari1
205 | OCC_235 | TSECL | ROKHIA - UNIT 9 | TRIPURA | D | Maintenance Work | 01/Mar/2026 | 09:00 | 01/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30843 | Sd may availed
206 | OCC_235 | TSECL | SURAJMANI NAGAR - 132KV - BUS 2 | TSECL | D | Maintenance Work | 27/Mar/2026 | 09:00 | 27/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30842 | SD may be availed subject to no outage of elements
207 | OCC_235 | TSECL | SURAJMANI NAGAR - 132KV - BUS 2 | TSECL | D | Maintenance Work | 21/Mar/2026 | 09:00 | 21/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30841 | SD may be availed subject to no outage of elements
208 | OCC_235 | TSECL | ROKHIA - 132KV - BUS 1 | TSECL | D | Maintenance Work | 01/Mar/2026 | 09:00 | 01/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30840 | SD may be availed subject to availability of 132kV Monarchak - Udaipur and 132kV Udaipur - Palatana. SPS at Monarchak need to be kept in off condition before availing shutdown.
209 | OCC_235 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Maintenance Work | 31/Mar/2026 | 09:00 | 31/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30839 | SD may be availed subject to availability of 132kV Badarpur - Karmaganj-Kumrghat link, 132kV AGTCCPP - Kumarghat and 132kV Kumarghat - Aizwal
210 | OCC_235 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Maintenance Work | 30/Mar/2026 | 09:00 | 30/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30838 | SD may be availed subject to the availabitiy of 132kV SM Nagar - Budhjungnagar,132kV Agartala - Budhjungnagar, 132kV SM Nagar(ISTS) - SM Nagar and 132kV PK Bari(ISTS) - PK bari
211 | OCC_235 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Maintenance Work | 28/Mar/2026 | 09:00 | 28/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30837 | SD may be availed subject to the availabitiy of 132kV SM Nagar(ISTS) - Budhjungnagar,132kV Agartala - Budhjungnagar, 132kV SM Nagar(ISTS) - SM Nagar and 132kV PK Bari(ISTS) - PK bari
212 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Maintenance Work | 27/Mar/2026 | 09:00 | 27/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30836 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
213 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Maintenance Work | 26/Mar/2026 | 09:00 | 26/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30835 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
214 | OCC_235 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Maintenance Work | 25/Mar/2026 | 09:00 | 25/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30834 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar, 132kV SM Nagar(ISTS) - Budhjungnagar
215 | OCC_235 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Maintenance Work | 24/Mar/2026 | 09:00 | 24/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30833 | S/D may be availed subject to availability of 132kV SM nagar(ISTS) - Budhjungnagar - SM Nagar, 132kV Palatana - SM Nagar and 132kV PK Bari - PK Bari
216 | OCC_235 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Maintenance Work | 23/Mar/2026 | 09:00 | 23/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30832 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari
217 | OCC_235 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Maintenance Work | 21/Mar/2026 | 09:00 | 21/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30831 | SD may be availed subject to availability of 132kV Badarpur - Karmaganj-Kumrghat link, 132kV AGTCCPP - Kumarghat and 132kV Kumarghat - Aizwal
218 | OCC_235 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Maintenance Work | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30830 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
219 | OCC_235 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Maintenance Work | 20/Mar/2026 | 09:00 | 20/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30829 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
220 | OCC_235 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Maintenance Work | 19/Mar/2026 | 09:00 | 19/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30828 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
221 | OCC_235 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Maintenance Work | 18/Mar/2026 | 09:00 | 18/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30827
222 | OCC_235 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Maintenance Work | 17/Mar/2026 | 09:00 | 17/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30826 | SD may be availed subject to the availability of 132kV PK bari-Dharmanagar and 132 Hailakandi-Dullavcherra link, Intimation to Assam
223 | OCC_235 | MEPTCL | LUMSNONG - 132KV - BUS 1 | MEPTCL | D | For replacing worn out conductors connecting across the bus to MCL, MPL and JUD feeders. | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30825 | S/D may be availed.132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C shall be kept in service.The availability of generation from Leshka will support real-time grid operation during shutdown period. Consented from Assam.
224 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Maintenance Work | 16/Mar/2026 | 09:00 | 16/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30824 | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
225 | OCC_235 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Maintenance Work | 13/Mar/2026 | 09:00 | 13/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30823 | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link. Monarchak Generation to be kept below 75 MW and SPS of Monarchak to be kept during the shutdown period.
226 | OCC_235 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Maintenance Work | 12/Mar/2026 | 09:00 | 12/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30822 | SD may be availed subject the availability of 132kV Palatana - SM Nagar, 132kV SM Nagar - Budhjungnagar - SM Nagar and 132kV PK Bari(ISTS) - PK Bari
227 | OCC_235 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | MEPTCL,AEGCL | D | Testing of 132kV Circuit Breaker and Distance Protection Relay (one after the other) | 06/Mar/2026 | 13:00 | 06/Mar/2026 | 17:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30821 | SD may be availed, intimation to SLDC Assam
228 | OCC_235 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | MEPTCL,AEGCL | D | Testing of 132kV Circuit Breaker and Distance Protection Relay (one after the other) | 06/Mar/2026 | 10:00 | 06/Mar/2026 | 13:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30820 | SD may be availed, intimation to SLDC Assam
229 | OCC_235 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | MEPTCL | D | Testing of 132kV Circuit Breaker and Distance Protection Relay (one after the other) | 03/Mar/2026 | 13:00 | 03/Mar/2026 | 17:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30819 | SD may be availed, intimation to SLDC Assam
230 | OCC_235 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Maintenance Work | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30818 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
231 | OCC_235 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | MEPTCL | D | Testing of 132kV Circuit Breaker and Distance Protection Relay (one after the other) | 03/Mar/2026 | 10:00 | 03/Mar/2026 | 13:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30817 | SD may be availed, intimation to SLDC Assam
232 | OCC_235 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | MEPTCL | D | Maintenance works | 25/Mar/2026 | 09:00 | 25/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30816 | SD may be availed, intimation to SLDC Assam
233 | OCC_235 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | MEPTCL | D | Maintenance works | 25/Mar/2026 | 09:00 | 25/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30815 | SD may be availed, intimation to SLDC Assam
234 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | TSECL | D | Maintenance Work | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30814 | Sd may be availed subject to the availability of 132kV SM Nagar(ISTS)-Budhjungnagar and 132kV Surajmaninagar(TSECL)-Budhjungnagar
235 | OCC_235 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | MEGHALAYA | D | Maintenance works | 12/Mar/2026 | 09:00 | 12/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30813 | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
236 | OCC_235 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | MEGHALAYA | D | Maintenance works | 12/Mar/2026 | 09:00 | 12/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30812 | SD may be availed subject to availability of , 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
237 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Maintenance Work | 09/Mar/2026 | 09:00 | 09/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30811 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
238 | OCC_235 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | MEGHALAYA | D | Maintenance works | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30810 | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
239 | OCC_235 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | MEGHALAYA | D | Maintenance works | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30809 | SD may be availed subject to availability of , 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
240 | OCC_235 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | MEPTCL | D | Jungle cutting in Tower Loc 236-249, loc 297-299 | 12/Mar/2026 | 09:00 | 12/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30808 | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra.
241 | OCC_235 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | For Tightening of nuts and bolts between location 126 to 123. | 26/Mar/2026 | 10:00 | 26/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30807 | S/D may be availed subject to availability of 220kV New Shillong - Mawngap 2
242 | OCC_235 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Maintenance Work | 07/Mar/2026 | 09:00 | 07/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30806 | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link. Monarchak Generation to be kept below 75 MW and SPS of Monarchak to be kept during the shutdown period.
243 | OCC_235 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | For Tightening of nuts and bolts between location 130 to 127. | 20/Mar/2026 | 10:00 | 20/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30805 | S/D may be availed subject to availability of 220kV New Shillong - Mawngap 2
244 | OCC_235 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Maintenance Work | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30804 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. FTC procedure to be followed before final charging of the line
245 | OCC_235 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | For Tightening of nuts and bolts between location 126 to 123. | 16/Mar/2026 | 10:00 | 16/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30803 | S/D may be availed subject to availability of 220kV New Shillong - Mawngap 2
246 | OCC_235 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Maintenance Work | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30802 | SD may be availed subject to the availability of 132kV Monarchak - udaipur and 132kV Monarchak - rokhia. Monarchak Generation to kept below 70 MW. SPS at Monarchak may be disabled before avaling shutdown.
247 | OCC_235 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | For Tightening of nuts and bolts between location 130 to 127. | 10/Mar/2026 | 10:00 | 10/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30801 | SD may be availed subject to the availability of 220kV New Shillong - Mawngai II
248 | OCC_235 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Maintenance Work | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30800 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
249 | OCC_235 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | For Tightening of nuts and bolts between location 136 & 134. | 03/Mar/2026 | 10:00 | 03/Mar/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ30799 | SD may be availed subject to the availability of 220kV New Shillong - Mawngai II
250 | OCC_235 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Maintenance Work | 02/Mar/2026 | 09:00 | 02/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30798 | SD may be availed subject to the availability of 132kV Sm Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari
251 | OCC_235 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Maintenance Work | 01/Mar/2026 | 09:00 | 01/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30795 | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link. Monarchak Generation to be kept below 75 MW and SPS of Monarchak to be kept during the shutdown period.
252 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Maintenance Work | 01/Mar/2026 | 09:00 | 01/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30796 | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
253 | OCC_235 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Maintenance Work | 01/Mar/2026 | 09:00 | 01/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30797 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
254 | OCC_235 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | ARUNACHAL PRADESH | D | Vegetation Clearance | 08/Mar/2026 | 09:00 | 08/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30788 | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
255 | OCC_235 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | ARUNACHAL PRADESH | D | Vegetation Clearance | 09/Mar/2026 | 09:00 | 09/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30787 | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
256 | OCC_235 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | DOP,ARUNACHAL PRADESH | D | Vegetation Clearance | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30786 | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
257 | OCC_235 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | DOP,ARUNACHAL PRADESH | D | Vegetation Clearance | 02/Mar/2026 | 09:00 | 02/Mar/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30784 | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
258 | OCC_235 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | MSPCL | D | Monthly change over of 3x105MVA transformer (R,B &Spare phase ICTs will be charged) | 09/Mar/2026 | 11:30 | 09/Mar/2026 | 13:00 | no load will be affected during the shutdown | Existing System Normal Maintenance Related Shut Down | RQ30783 | SD may be availed subject to the Imphal-Yurembam-Yiangangpopki-KongbaThubal-kakching-Churachandpur-Ningthoukhong link.
259 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 11/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30782 | S/D may be availed
260 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-1 | STERLITE | C | Shutdown required for reconductoring of Brahmaputra River Crossing | 08/Mar/2026 | 09:00 | 11/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30781 | S/D may be availed
261 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 10/Mar/2026 | 09:00 | 10/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30780 | S/D may be availed
262 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 09/Mar/2026 | 09:00 | 09/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30779 | S/D may be availed
263 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 08/Mar/2026 | 09:00 | 08/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30778 | S/D may be availed
264 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30777 | SD deferred as punched twice
265 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 05/Mar/2026 | 09:00 | 05/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30776 | SD deferred as punched twice
266 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 04/Mar/2026 | 09:00 | 04/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30775 | SD deferred as punched twice
267 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-2 | STERLITE | D | Shutdown required for reconductoring of Brahmaputra River Crossing | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30774 | SD deferred as punched twice
268 | OCC_235 | STERLITE | 220KV-BONGAIGAON-NANGALBIBRA-1 | STERLITE | C | Shutdown required for reconductoring of Brahmaputra River Crossing | 03/Mar/2026 | 09:00 | 06/Mar/2026 | 16:00 | Shutdown required | Existing System Improvement Related Shut Down | RQ30765 | SD deferred as punched twice
269 | OCC_235 | NEEPCO | TUIRIAL - UNIT 1 | NEEPCO | C | Annual Planned Maintenance of Unit-1 | 11/Mar/2026 | 00:00 | 31/Mar/2026 | 23:59 |  | Existing System Normal Maintenance Related Shut Down | RQ30764 | SD deferred as SD already approved on post OCC
270 | OCC_235 | NEEPCO | TUIRIAL - UNIT 2 | NEEPCO | C | Seal Replacement of MIV in Unit-2 | 01/Mar/2026 | 00:00 | 10/Mar/2026 | 23:59 |  | Existing System Normal Maintenance Related Shut Down | RQ30763 | SD deferred as SD already approved on post OCC
271 | OCC_235 | NEEPCO | TUIRIAL - UNIT 1 | NEEPCO | C | Seal Replacement of MIV in Unit-1 | 01/Mar/2026 | 00:00 | 10/Mar/2026 | 23:59 |  | Existing System Normal Maintenance Related Shut Down | RQ30762 | SD deferred as SD already approved on post OCC
272 | OCC_235 | NEEPCO | KOPILI - UNIT 1 | NEEPCO | C | Annual Plant Maintenance | 01/Mar/2026 | 00:00 | 16/Mar/2026 | 00:00 |  | Existing System Normal Maintenance Related Shut Down | RQ30750 | SD deferred as SD already approved on post OCC
273 | OCC_235 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | NEEPCO | D | Installation of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 06/Mar/2026 | 09:00 | 06/Mar/2026 | 15:00 | Shutdown is required on 06.03.2026 from 09:00 Hrs to 15:00 Hrs | Existing System Improvement Related Shut Down | RQ30748 | SD May be availed subject to availability of 132/33kV ICT-2 at Panyor
274 | OCC_235 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | NEEPCO | D | Dismantling of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 03/Mar/2026 | 09:00 | 03/Mar/2026 | 15:00 | Shutdown is required on 03.03.2026 from 09:00 Hrs to 15:00 Hrs | Existing System Improvement Related Shut Down | RQ30747 | SD May be availed subject to availability of 132/33kV ICT-2 at Panyor
275 | OCC_235 | NEEPCO | AGTCCPP - STG 2 | NEEPCO | C | Steam Turbine Minor Overhauling and Generator & Generator Circuit Breaker Overhauling | 20/Mar/2026 | 00:00 | 03/Apr/2026 | 23:59 |  | Existing System Normal Maintenance Related Shut Down | RQ30746 | SD may be availed. Consent from Beneficiaries is required.
276 | OCC_235 | NEEPCO | AGTCCPP - STG 1 | NEEPCO | C | Steam Turbine Minor Overhauling and Generator & Generator Circuit Breaker Overhauling | 04/Mar/2026 | 00:00 | 18/Mar/2026 | 23:59 |  | Existing System Normal Maintenance Related Shut Down | RQ30745 | SD may be availed. Consent from Beneficiaries is required.
277 | OCC_235 | NEEPCO | DOYANG - UNIT 2 | NEEPCO | C | Installation and commissiong of New 28.5 MVA GT and APM works | 01/Mar/2026 | 00:00 | 23/Mar/2026 | 23:59 | Installation and commissiong of New 28.5 MVA GT and APM works | Existing System Improvement Related Shut Down | RQ30744 | SD may be availed. Consent from Beneficiaries is required.
278 | OCC_235 | NEEPCO | KAMENG HEP - UNIT 2 | NEEPCO | C | Annual Plant Maintenance | 16/Mar/2026 | 00:00 | 30/Mar/2026 | 23:59 | APM | Existing System Normal Maintenance Related Shut Down | RQ30741 | SD may be availed. Consent from Beneficiaries is required.
279 | EROCC | ENICL | 220KV-ALIPURDUAR (PG)-SALAKATI-1 | ERPC | D | S/d for replacement of faulty TL LA | 12/Mar/2026 | 8:00 | 12/Mar/2026 | 18:00 |  |  |  | SD may be vailed subjected to availability of other inter regional elements in ER-NER corridor
280 | EROCC | ENICL | 220KV-ALIPURDUAR (PG)-SALAKATI-2 | ERPC | D | S/d for replacement of faulty TL LA | 13/Mar/2026 | 8:00 | 13/Mar/2026 | 18:00 |  |  |  | SD may be vailed subjected to availability of other inter regional elements in ER-NER corridor