## Sheet1
sl. no | occ number | name of requesting agency | element name | owner | daily/ continous | reason | shutdown start date | shutdown start time | shutdown end date | shutdown end time | requester remarks | reference number | Study comments
1 | OCC_236 | AEGCL | 132KV-UMTRU-SARUSAJAI-2 | MEPTCL | D | PREVENTIVE MAINTENANCE | 30/Apr/2026 | 10:00 | 30/Apr/2026 | 14:00 | AGM SARUSAJAI | RQ31276 | SD may be availed, intimation to SLDC Assam
2 | OCC_236 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 30/Apr/2026 | 09:00 | 30/Apr/2026 | 16:00 |  | RQ31240 | S/D may be availed subject to availability of 132KV Budhjungnagar- Surajmaninagar and 132kV Surajmaninagar - Surajmaninagar (Indi-grid) line and 132kV Buddhjunnagar-Agartala.
3 | OCC_236 | NETCL | 400KV-BONGAIGAON-BYRNIHAT (KILLING) | MEPTCL,NETC | D | Tightening of loose Jumper N&B, Replacement of rusted Jumper N&B. | 29/Apr/2026 | 11:00 | 29/Apr/2026 | 14:00 | Put up for approval in the 235th OCCM. | RQ31180 | S/D may be availed subject to availability of 400 kV Bongaigaon – Azara, 400 kV Silchar – Killing, 400 kV Silchar – Azara, 220 kV Agia – BTPS D/C, 220 kV Balipara – Sonabil – Samaguri D/C, 220 kV Samaguri – Sonapur – Sarusajai link and 220 kV Samaguri – Jawaharnagar – Sarusajai link. The combined loading of the 220 kV BTPS–Agia D/C line should be maintained below 240 MW during the shutdown period to ensure safe and reliable operation.
4 | OCC_236 | AEGCL | 132KV-UMTRU-SARUSAJAI-1 | MEPTCL | D | PREVENTIVE MAINTENANCE | 29/Apr/2026 | 10:00 | 29/Apr/2026 | 14:00 | AGM SARUSAJAI | RQ31275 | SD may be availed, intimation to SLDC Assam
5 | OCC_236 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 127 to 125. | 29/Apr/2026 | 10:00 | 29/Apr/2026 | 15:00 | Avail | RQ31204 | SD may be availed subject to availability of 220kV New Shillong- Mawngap 1
6 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 29/Apr/2026 | 09:00 | 29/Apr/2026 | 16:00 |  | RQ31238 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link,
7 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Pre-Monsoon Maintenance Work | 29/Apr/2026 | 09:00 | 29/Apr/2026 | 16:00 |  | RQ31239 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
8 | OCC_236 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | PREVENTIVE MAINTENANCE | 29/Apr/2026 | 09:00 | 29/Apr/2026 | 16:00 | RE PAILAPOOL | RQ31294 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
9 | OCC_236 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING LOC 235 TO 247 | 30/Apr/2026 | 8:00 | 30/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31302 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
10 | OCC_236 | NEEPCO | 132KV-PARE-ITANAGAR-1 | NEEPCO,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 29/Apr/2026 | 07:00 | 29/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31259 | SD may be availed subject to availability of 132kV Panyor-Lekhi-Nirjuli link, 132kV BNC(PG)-Itanagar, 132kV Gohpur-Itanagar & 132kV Nirjuli-Gohpur-North Lakhimpur-Pare link.
11 | OCC_236 | NEEPCO | 132KV-RANGANADI-PARE-2 | NEEPCO,DOP,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 29/Apr/2026 | 07:00 | 29/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31262 | SD may be availed subject Itanagar-BNC and 132 kV Itanagar-Gohpur line.
12 | OCC_236 | AEGCL | 220KV-TINSUKIA-NRPP-1 | ASSAM | D | CORRIDOR CLEANING LOC 1 TO 30 | 28/Apr/2026 | 10:00 | 28/Apr/2026 | 16:00 | AGM TINSUKIA | RQ31274 | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
13 | OCC_236 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 28/Apr/2026 | 09:00 | 28/Apr/2026 | 16:00 |  | RQ31237 | SD may be availed subject to availability of 132 kV SM Nagar(ISTS) -SM Nagar line and 132kV PK Bari-PK Bari line
14 | OCC_236 | NEEPCO | 132KV-PARE-ITANAGAR-1 | NEEPCO,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 28/Apr/2026 | 07:00 | 28/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31258 | SD may be availed subject to availability of 132kV Panyor-Lekhi-Nirjuli link, 132kV BNC(PG)-Itanagar, 132kV Gohpur-Itanagar & 132kV Panyor-Pare-Nirjuli-Gohpur-North Lakhimpur-Pare link.
15 | OCC_236 | NEEPCO | 132KV-RANGANADI-PARE-2 | NEEPCO,DOP,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 28/Apr/2026 | 07:00 | 28/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31261 | SD may be availed subject Itanagar-BNC and 132 kV Itanagar-Gohpur line.
16 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Pre-Monsoon Maintenance Work | 27/Apr/2026 | 09:00 | 27/Apr/2026 | 16:00 |  | RQ31236 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
17 | OCC_236 | POWERGRID | 220KV-MISA-SAMAGURI-2 | POWERGRID | D | For testing of TBC Scheme for Samaguri-2 line | 27/Apr/2026 | 09:00 | 27/Apr/2026 | 11:00 |  | RQ31335 | The SD may be availed subject to availability of 220kV Misa - Samaguri 1, 220kV Azara-Sausajai D/C, 220 kV Balipara-Sonabil D/C- Samaguri D/C, 220 kV Mariani - Samaguri. SPS for 220 kV Samaguri- Misa D/C to be kept off when the combined loading of 220 kV Balipara-Sonabil D/C and 220 kV Samaguri- Misa 1 is less than 370 MW.
18 | OCC_236 | POWERGRID | TIE BAY () OF 400KV-BALIPARA-BONGAIGAON-4 AND 400KV-BALIPARA-KAMENG-1 @BALIPARA - 400KV | POWERGRID | C | CB mechnism overhualing | 27/Apr/2026 | 09:00 | 30/Apr/2026 | 16:00 |  | RQ31400 | SD may be availed subject to availability of 400kV Balipara - Bongaigaon IV main bay and 400kV Balipara - Kameng I main bay at 400kV Balipara S/S
19 | OCC_236 | POWERGRID | 220 KV SAMAGURI 2 BAY (210) AT MISA | POWERGRID | C | For CB Mechanism overhauling. (Line may be charged through BC bay). All elements shall be in one bus and Samaguri-2 line shall be in service through TBC bay | 27/Apr/2026 | 09:00 | 29/Apr/2026 | 16:00 |  | RQ31404 | SD may be availed subject to no outage of elements.
20 | OCC_236 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 27/Apr/2026 | 09:00 | 27/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31300 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
21 | OCC_236 | POWERGRID | 400KV-PALATANA-SILCHAR-1 L/R@ SILCHAR - 400KV | POWERGRID | D | AMP WORKS OF CB | 27/Apr/2026 | 08:00 | 27/Apr/2026 | 16:00 |  | RQ31416 | SD may be availed
22 | OCC_236 | NEEPCO | 132KV-PARE-ITANAGAR-1 | NEEPCO,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 27/Apr/2026 | 07:00 | 27/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31257 | SD may be availed subject to availability of 132kV Panyor-Lekhi-Nirjuli link, 132kV BNC(PG)-Itanagar, 132kV Gohpur-Itanagar & 132kV Panyor-Pare-Nirjuli-Gohpur-North Lakhimpur-Pare link. Consent from AP
23 | OCC_236 | NEEPCO | 132KV-RANGANADI-PARE-2 | NEEPCO,DOP,ARUNACHAL PRADESH | D | Day time S/D required for vegetation clearance for LILO-2 portion of NEEPCO for 3 days from 27-04-26 to 29-04-26 | 27/Apr/2026 | 07:00 | 27/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-04-26 for vegetation clearance of LILO portion of NEEPCO | RQ31260 | SD may be availed subject Itanagar-BNC and 132 kV Itanagar-Gohpur line. Consent from AP
24 | OCC_236 | TSECL | 132KV-KAILASOHAR-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31232 | SD may be availed
25 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31233 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
26 | OCC_236 | TSECL | 132KV-KAMALPUR-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31234 | Sd may be availed subject to the availability of Agartala-Mohanpur-Dhalabill-Kamalpur link
27 | OCC_236 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31235 | Sd may be availed subject to the avavilability of 132kV Badarpur-karimganj-kumarghat-Agartala(RC Nagar) link
28 | OCC_236 | TSECL | P K BARI - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31249 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link, Agartala-AGTCCPP D/C, Agartala-Mohanpur-Dhalabil-Kamalpur link, 132kV Agaratala-Suramaningar-Surajmaninagar(ISTS)-PK bari-Silchar link
29 | OCC_236 | TSECL | 132KV-AGTCCPP-P K BARI-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31229 | Sd may be availed subject to the availability of 132kV AGTCCPP-PK Bari ckt 2 and 132kV AGTCPP-Agartala D/C. Intimation to NEEPCO and Powergrid.
30 | OCC_236 | TSECL | 132KV-AGTCCPP-P K BARI-2 | INDIGRID | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31230 | Sd may be availed subject to the availability of 132kV AGTCCPP-PK Bari ckt 1 and 132kV AGTCPP-Agartala D/C. Intimation to NEEPCO and Powergrid.
31 | OCC_236 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 26/Apr/2026 | 09:00 | 26/Apr/2026 | 16:00 |  | RQ31231 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
32 | OCC_236 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 25/Apr/2026 | 09:00 | 25/Apr/2026 | 16:00 |  | RQ31227 | S/D may be availed. No power supply at Udaipur.
33 | OCC_236 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 25/Apr/2026 | 09:00 | 25/Apr/2026 | 16:00 |  | RQ31228 | /D may be availed. No power supply at Udaipur.tion may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown.
34 | OCC_236 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 25/Apr/2026 | 09:00 | 25/Apr/2026 | 16:00 |  | RQ31248 | S/D may be availed. No power supply at Udaipur.
35 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-2 L/R@ BONGAIGAON - 400KV | POWERGRID | D | AMP works. Line Switching required for opening of the Reactor Isolator | 25/Apr/2026 | 09:00 | 25/Apr/2026 | 16:00 |  | RQ31414 | SD may be availed
36 | OCC_236 | NEEPCO | 132KV-PARE-NORTH LAKHIMPUR-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 25/Apr/2026 | 07:00 | 25/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31253 | SD may be availed subject to the availability of 132kV Pare-nirjuli-North Lakhimpur link, North Lakhimpur-Gohpur-BNC link. Consent from Assam
37 | OCC_236 | NEEPCO | 132KV-PARE-NIRJULI-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 25/Apr/2026 | 07:00 | 25/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31256 | Sd may be availed subject to availability of 132kV Pare-north Lakhimpur-gohpur-nirjuli link and Gohpur -BNC link. Intimation to Sterlite and NERTS
38 | OCC_236 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Pre-Monsoon Maintenance Work | 24/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 |  | RQ31226 | SD may be allowed subject to the availability of 132kV PK-PK Bari , 132kV Surajamaninagar(ISTS)-Budhjungnagar-Surajmaninagar(ST), Palatana-Surajmaninagar link
39 | OCC_236 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-1 | PGCB,POWERGRID | D | AMP works | 24/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 |  | RQ31326 | SD may be availed subject to the availabilityof 132kV Surajmaninagar-Comilla 2, NLDC consent is required
40 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 24/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 |  | RQ31381 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
41 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -4 | 24/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 |  | RQ31385 | Sd may be availed
42 | OCC_236 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 24/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31298 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
43 | OCC_236 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | POWERGRID | D | Rectification of jumper dropper LA to CVT at Jiribam SS | 24/Apr/2026 | 08:00 | 24/Apr/2026 | 16:00 |  | RQ31321 | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh. Consent from to Manipur
44 | OCC_236 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 24/Apr/2026 | 08:00 | 24/Apr/2026 | 16:00 | AGM MARIANI | RQ31269 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
45 | OCC_236 | NEEPCO | 132KV-PARE-NORTH LAKHIMPUR-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 24/Apr/2026 | 07:00 | 24/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31252 | SD may be availed subject to the availability of 132kV Pare-nirjuli-North Lakhimpur link, North Lakhimpur-Gohpur-BNC link. Consent from Assam
46 | OCC_236 | NEEPCO | 132KV-PARE-NIRJULI-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 24/Apr/2026 | 07:00 | 24/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31255 | Sd may be availed subject to availability of 132kV Pare-north Lakhimpur-gohpur-nirjuli link and Gohpur -BNC link
47 | OCC_236 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 23/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 |  | RQ31225 | S/D may be availed subject to availability of 132KV Budhjungnagar- Surajmaninagar and 132kV Surajmaninagar - Surajmaninagar (Indi-grid) line and 132kV Buddhjunnagar-Agartala.
48 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 23/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 |  | RQ31380 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
49 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -4 | 23/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 |  | RQ31384 | Sd may be availed
50 | OCC_236 | POWERGRID | FILTER BANK3 TIE BAY AT BNC | POWERGRID | D | AMP works | 23/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 |  | RQ31399 | SD may be availed. NLDc consent is required
51 | OCC_236 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 23/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31296 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s and Balipara-Sonabil-Samaguri-Sonapur/jawaharnagar-Azara link should be kept in service.
52 | OCC_236 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 17 TO 27 | 18/Apr/2026 | 8:00 | 18/Apr/2026 | 16:00 | AGM SARUSAJAI & AGM SAMAGURI | RQ31306 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
53 | OCC_236 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 23/Apr/2026 | 08:00 | 23/Apr/2026 | 16:00 | AGM MARIANI | RQ31268 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
54 | OCC_236 | AEGCL | 132KV-GOHPUR-NALKATA-2 | POWERGRID | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 176 TO 249 | 23/Apr/2026 | 08:00 | 23/Apr/2026 | 15:00 | AGM NORTH LAKHIMPUR T&T | RQ31285 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
55 | OCC_236 | NEEPCO | 132KV-PARE-NORTH LAKHIMPUR-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 23/Apr/2026 | 07:00 | 23/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31251 | SD may be availed subject to the availability of 132kV Pare-nirjuli-North Lakhimpur link, North Lakhimpur-Gohpur-BNC link
56 | OCC_236 | NEEPCO | 132KV-PARE-NIRJULI-1 | NEEPCO,STERLITE | D | Day time S/D required for vegetation clearance. | 23/Apr/2026 | 07:00 | 23/Apr/2026 | 14:00 | Day time S/D required for vegetation clearance for 3 days from 23-04-26 to 26-0426 | RQ31254 | Sd may be availed subject to availability of 132kV Pare-north Lakhimpur-gohpur-nirjuli link and Gohpur -BNC link
57 | OCC_236 | AEGCL | 220KV-TINSUKIA-NTPS-1 | ASSAM | D | CORRIDOR CLEANING LOC 68 TO 100 | 22/Apr/2026 | 10:00 | 22/Apr/2026 | 16:00 | AGM TINSUKIA | RQ31273 | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
58 | OCC_236 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 130 to 128. | 22/Apr/2026 | 10:00 | 22/Apr/2026 | 15:00 | Avail | RQ31201 | SD may be availed subject to availability of 220kV New Shillong- Mawngap 1
59 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 22/Apr/2026 | 09:00 | 22/Apr/2026 | 16:00 |  | RQ31224 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
60 | OCC_236 | POWERGRID | 220KV-MISA-SAMAGURI-1 | POWERGRID | D | For testing of TBC Scheme for Samaguri-1 line | 22/Apr/2026 | 09:00 | 22/Apr/2026 | 11:00 |  | RQ31334 | The SD may be availed subject to availability of 220kV Misa - Samaguri 2, 220kV Azara-Sausajai D/C, 220 kV Balipara-Sonabil D/C, 220 kV Mariani - Samaguri. SPS for 220 kV Samaguri- Misa D/C to be kept off when the combined loading of 220 kV Balipara-Sonabil D/C and 220 kV Samaguri- Misa 2 is less than 370 MW.
61 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 22/Apr/2026 | 09:00 | 22/Apr/2026 | 16:00 |  | RQ31379 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
62 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -4 | 22/Apr/2026 | 09:00 | 22/Apr/2026 | 16:00 |  | RQ31383 | Sd may be availed
63 | OCC_236 | POWERGRID | TIE BAY () OF BISWANATH CHARIALI - 400KV-FILTER BANK-1 AND BISWANATH CHARIALI - 400KV-FILTER BANK-2 @BISWANATH CHARIALI - 400KV | POWERGRID | D | AMP works | 22/Apr/2026 | 09:00 | 22/Apr/2026 | 16:00 |  | RQ31398 | Sd may be availed subject to no outage of element
64 | OCC_236 | POWERGRID | 220 KV SAMAGURI 1 BAY (211) AT MISA | POWERGRID | C | For CB Mechanism overhauling. (Line may be charged through BC bay). All elements shall be in one Bus and Samaguri-1 line shall be in service through TBC bay | 22/Apr/2026 | 09:00 | 24/Apr/2026 | 16:00 |  | RQ31403 | Sd may be aviled subject to no outage of elements.
65 | OCC_236 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | MEPTCL,AEGCL | D | Maintenance work | 22/Apr/2026 | 08:00 | 22/Apr/2026 | 16:00 | Avail | RQ31220 | SD may be availed, intimation to SLDC Assam
66 | OCC_236 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | MEPTCL,AEGCL | D | Maintenance work | 22/Apr/2026 | 08:00 | 22/Apr/2026 | 16:00 | Avail | RQ31222 | SD may be availed, intimation to SLDC Assam
67 | OCC_236 | POWERGRID | 132KV-KARIMGANJ (AS)-KUMARGHAT-1 | POWERGRID | D | For replacement of flashover mark insulator at Loc No 298 | 22/Apr/2026 | 08:00 | 22/Apr/2026 | 16:00 |  | RQ31322 | Sd may be availed subject to the availability of 132kV Badarpur-Karimganj link
68 | OCC_236 | POWERGRID | 132KV/33KV IMPHAL(PG)-ICT-2 | POWERGRID | D | AMP works and Replacment of Aircell | 22/Apr/2026 | 08:00 | 22/Apr/2026 | 16:00 |  | RQ31406 | SD may be availed subject to the availability of other ICT. Consented from Manipur
69 | OCC_236 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 176 TO 249 | 22/Apr/2026 | 08:00 | 22/Apr/2026 | 15:00 | AGM NORTH LAKHIMPUR T&T | RQ31283 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
70 | OCC_236 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 19/Apr/2026 | 8:00 | 19/Apr/2026 | 16:00 | AGM NAGAON T&T | RQ31308 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
71 | OCC_236 | MEPTCL | 220KV/132KV MAWNGAP-ICT-2 | MEGHALAYA | D | Checking the NIFPS Fire Detector (FD) trip | 21/Apr/2026 | 10:00 | 21/Apr/2026 | 16:00 | Avail | RQ31250 | SD may be availed subject to the availability of 220/132kV Mawngap ICT 1, killing-EPIP-Umtru-Umiam III-Umiam I link and Khleiriat-Mustem-Nehu-Umaim-Umaim 1 link.
72 | OCC_236 | POWERGRID | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | AMP works | 19/Apr/2026 | 8:00 | 19/Apr/2026 | 16:00 |  | RQ31328 | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
73 | OCC_236 | POWERGRID | 132KV-BISWANATH CHARIALI-ITANAGAR-2 | INDIGRID | D | AMP works | 21/Apr/2026 | 09:00 | 21/Apr/2026 | 16:00 |  | RQ31345 | SD may be availed
74 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 21/Apr/2026 | 09:00 | 21/Apr/2026 | 16:00 |  | RQ31378 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
75 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -4 | 21/Apr/2026 | 09:00 | 21/Apr/2026 | 16:00 |  | RQ31382 | SD may be availed
76 | OCC_236 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31221 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. before final charging of the line
77 | OCC_236 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31223 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
78 | OCC_236 | TSECL | SURAJMANI NAGAR - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 21/Apr/2026 | 09:00 | 21/Apr/2026 | 16:00 |  | RQ31247 | Sd may be availed subject to no outage of elements. All element shifted to Main Bus 2 online before taking SD. 132kV PK Bari(ISTS)-PK Bari, 132kV Surajmaningar(ISTS)-Surajmaningar, 132kV Surajmaningar(ISTS)- Budhjungnagar line must be in service.Intiamtion to NLDC
79 | OCC_236 | POWERGRID | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | AMP works | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31327 | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
80 | OCC_236 | POWERGRID | 132KV-BISWANATH CHARIALI-ITANAGAR-1 | INDIGRID | D | AMP works | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31344 | SD may be availed
81 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31377 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 4
82 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -3 | 20/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31389 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
83 | OCC_236 | POWERGRID | 400 KV BGTPP 2 BAY AT BONGAIGAON | POWERGRID | C | CB mechnism overhualing | 20/Apr/2026 | 09:00 | 23/Apr/2026 | 16:00 |  | RQ31397 | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon II & 80MVAR BR III, IV tie bay and 80 MVAR BR III, IV main bay at Bogaingaon
84 | OCC_236 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 20/Apr/2026 | 08:00 | 20/Apr/2026 | 16:00 | AGM NAGAON T&T | RQ31307 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
85 | OCC_236 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 314 TO 238 | 20/Apr/2026 | 06:00 | 20/Apr/2026 | 16:00 | AGM SAMAGURI | RQ31280 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
86 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31216 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
87 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Pre-Monsoon Maintenance Work | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31217 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
88 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31218 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
89 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-AGTCCPP-2 | POWERGRID | D | Pre-Monsoon Maintenance Work | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31219 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
90 | OCC_236 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1 (Section 3) | TSECL | D | Pre-Monsoon Maintenance Work | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 | 132kV Agartala Bus I (Section III) | RQ31246 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
91 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31376 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 4
92 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -3 | 19/Apr/2026 | 09:00 | 19/Apr/2026 | 16:00 |  | RQ31388 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 3
93 | OCC_236 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 18/Apr/2026 | 09:30 | 18/Apr/2026 | 16:00 | RE RUPAI | RQ31264 | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
94 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 18/Apr/2026 | 09:00 | 18/Apr/2026 | 16:00 |  | RQ31375 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 4
95 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -3 | 18/Apr/2026 | 09:00 | 18/Apr/2026 | 16:00 |  | RQ31387 | Sd may be availed
96 | OCC_236 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 18/Apr/2026 | 09:00 | 18/Apr/2026 | 16:00 |  | RQ31214 | SD may be availed subject to availability of 132 kV Monarchak-Udaipur line. Mornarchak generation may be limited to 70 MW during SD period.
97 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 17/Apr/2026 | 09:00 | 17/Apr/2026 | 16:00 |  | RQ31374 | Sd may be availed subject to the availability of 400kV Baliapara-Bongaigaon 1,2 and 4
98 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-4 | POWERGRID | D | AR in Non -Auto mode required for insulator replacment works in 400 KV Bongaigaon - Balipara -3 | 17/Apr/2026 | 09:00 | 17/Apr/2026 | 16:00 |  | RQ31386 | Sd may be availed
99 | OCC_236 | POWERGRID | 400 KV BISWANATH CHARIALI 3 MAIN BAY (415) AT BALIPARA | POWERGRID | C | CB mechnism overhualing | 17/Apr/2026 | 09:00 | 20/Apr/2026 | 16:00 |  | RQ31396 | SD may be availed, BNC 3 shares dia with Bongaigaon 1
100 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 17/Apr/2026 | 09:00 | 17/Apr/2026 | 16:00 |  | RQ31213 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
101 | OCC_236 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 1 TO 20 | 17/Apr/2026 | 08:30 | 17/Apr/2026 | 16:30 | AGM SARUSAJAI | RQ31278 | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
102 | OCC_236 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | NAGALAND,DOP | D | vegetation clearance | 17/Apr/2026 | 08:00 | 17/Apr/2026 | 16:00 |  | RQ31174 | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C
103 | OCC_236 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | Tightening of nuts and bolts between Tower Location 127 to 125. | 16/Apr/2026 | 10:00 | 16/Apr/2026 | 15:00 | Avail | RQ31200 | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
104 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 16/Apr/2026 | 09:00 | 16/Apr/2026 | 16:00 |  | RQ31212 | S/D may be availed 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
105 | OCC_236 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | NAGALAND,DOP | D | vegetation clearance | 16/Apr/2026 | 08:00 | 16/Apr/2026 | 16:00 |  | RQ31173 | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C
106 | OCC_236 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance work | 16/Apr/2026 | 08:00 | 16/Apr/2026 | 16:00 | Avail | RQ31211 | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing. Intimation to NERTS
107 | OCC_236 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance work | 23/Apr/2026 | 8:00 | 23/Apr/2026 | 16:00 | Avail | RQ31215 | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing. Intimation to NERTS
108 | OCC_236 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | NAGALAND,DOP | D | vegetation clearance | 15/Apr/2026 | 08:00 | 15/Apr/2026 | 16:00 |  | RQ31172 | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C
109 | OCC_236 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | NAGALAND,DOP | D | vegetation clearance | 14/Apr/2026 | 08:00 | 14/Apr/2026 | 16:00 |  | RQ31171 | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C
110 | OCC_236 | POWERGRID | 400 KV BGTPP 1 BAY AT BONGAIGAON | POWERGRID | C | CB mechnism overhualing | 13/Apr/2026 | 09:00 | 16/Apr/2026 | 16:00 |  | RQ31395 | SD may be availed subject to availability of 400kV BGTPP - Bongaigaon I & 400kV Byrnihat - Bongaigaon tie bay and 400kV 400kV Byrnihat - Bongaigaon main bay at 400kV Bongaigaon S/S
111 | OCC_236 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-1 L/R@ BONGAIGAON - 400KV | POWERGRID | D | AMP works. Line Switching required for opening of the Reactor Isolator | 13/Apr/2026 | 09:00 | 13/Apr/2026 | 16:00 |  | RQ31415 | Sd may be availed subject to no outage of elements
112 | OCC_236 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 13/Apr/2026 | 09:00 | 13/Apr/2026 | 16:00 |  | RQ31208 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar
113 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 13/Apr/2026 | 09:00 | 13/Apr/2026 | 16:00 |  | RQ31210 | S/D may be availed 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
114 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 13/Apr/2026 | 08:00 | 13/Apr/2026 | 16:00 |  | RQ31355 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
115 | OCC_236 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | NAGALAND,DOP | D | vegetation clearance | 13/Apr/2026 | 08:00 | 13/Apr/2026 | 16:00 |  | RQ31170 | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C
116 | OCC_236 | TSECL | BUDHJANGNAGAR - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/Apr/2026 | 09:00 | 12/Apr/2026 | 16:00 |  | RQ31245 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
117 | OCC_236 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/Apr/2026 | 09:00 | 12/Apr/2026 | 16:00 |  | RQ31202 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
118 | OCC_236 | TSECL | 132KV-BODHJUNGNAGAR-JIRANIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/Apr/2026 | 09:00 | 12/Apr/2026 | 16:00 |  | RQ31203 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
119 | OCC_236 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 12/Apr/2026 | 09:00 | 12/Apr/2026 | 16:00 |  | RQ31205 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
120 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/Apr/2026 | 09:00 | 12/Apr/2026 | 16:00 |  | RQ31206 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
121 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 12/Apr/2026 | 08:00 | 12/Apr/2026 | 16:00 |  | RQ31354 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
122 | OCC_236 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1 (Section 2) | TSECL | D | Pre-Monsoon Maintenance Work | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 | 132kV Agartala Bus I (Section II) | RQ31244 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
123 | OCC_236 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31329 | SD may be availed subject to availability of 220kV Misa-Diampur-II ckt.
124 | OCC_236 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-2 | POWERGRID | D | AR in Non -auto mode required for insulator replacment works in 220 Misa - Dimapur - 1 | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31332 | SD may be availed subject to availability of 220kV Misa-Diampur-I ckt.
125 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-MOHANPUR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31193 | SD may be availed subject to the availability of 132kV PK Bari-Kamalpur-Dhalabil-Mohanpur link
126 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-AGTCCPP-1 | POWERGRID | D | Pre-Monsoon Maintenance Work | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31194 | SD may be availed subject to the availabitiy of 132kV Agartala-AGTCCPP-2, 132kV AGTCPP-PK Bari D/C
127 | OCC_236 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 11/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31195 | SD may be availed subject to availability of 132 kV SM Nagar(ISTS) -SM Nagar line and 132kV PK Bari-PK Bari
128 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 11/Apr/2026 | 08:00 | 11/Apr/2026 | 16:00 |  | RQ31353 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
129 | OCC_236 | NAGALAND | 132KV-DIMAPUR-DIMAPUR(PG)-2 | NAGALAND,DOP | D | Substation Maintainace | 11/Apr/2026 | 06:00 | 11/Apr/2026 | 09:00 |  | RQ31168 | Sd may be availed. 132kV Dimapur(NL) S/s will be under blackout.
130 | OCC_236 | NAGALAND | 132KV-DIMAPUR-DIMAPUR(PG)-1 | NAGALAND,POWERGRID,DOP | D | Substation Maintainace | 11/Apr/2026 | 06:00 | 11/Apr/2026 | 09:00 |  | RQ31169 | Sd may be availed. 132kV Dimapur(NL) S/s will be under blackout.
131 | OCC_236 | NETCL | 400KV-AZARA-BONGAIGAON-1 | NETC,AEGCL | D | Tightening of loose Jumper N&B, Replacement of rusted Jumper N&B. | 10/Apr/2026 | 11:00 | 10/Apr/2026 | 14:00 | Put up for approval in the 236th OCCM. | RQ31198 | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon.
132 | OCC_236 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 10/Apr/2026 | 09:30 | 10/Apr/2026 | 16:00 | RE RUPAI | RQ31289 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link
133 | OCC_236 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 10/Apr/2026 | 09:00 | 10/Apr/2026 | 16:00 |  | RQ31192 | SD may be availed subject to availability of 132 kV Monarchak-Udaipur line. Mornarchak generation may be limited to 70 MW during SD period.
134 | OCC_236 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | AEGCL | D | ROUTINE TESTING | 10/Apr/2026 | 09:00 | 10/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31263 | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
135 | OCC_236 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 10/Apr/2026 | 09:00 | 10/Apr/2026 | 16:00 | RE BOKAJAN | RQ31270 | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
136 | OCC_236 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 229 TO 235 | 10/Apr/2026 | 08:30 | 10/Apr/2026 | 16:30 | AGM SARUSAJAI | RQ31304 | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
137 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 10/Apr/2026 | 08:00 | 10/Apr/2026 | 16:00 |  | RQ31352 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
138 | OCC_236 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 10/Apr/2026 | 08:00 | 10/Apr/2026 | 16:00 | AGM NAGAON T&T & AGM MNI | RQ31311 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
139 | OCC_236 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | MSPCL | D | Monthly change of 3*105MVA transfer (R,Y&sphare will be charged) | 09/Apr/2026 | 11:30 | 09/Apr/2026 | 13:30 | No load will be affected | RQ31418 | SD may be availed subject to the Imphal-Yurembam-Yiangangpopki-KongbaThubal-kakching-Churachandpur-Ningthoukhong link.
140 | OCC_236 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 266 TO 272 | 09/Apr/2026 | 10:00 | 09/Apr/2026 | 16:00 | RE DULLAVCHERRA & AGM PNG | RQ31315 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Tripura
141 | OCC_236 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 09/Apr/2026 | 09:30 | 09/Apr/2026 | 16:00 | AGM PANCHGRAM | RQ31277 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
142 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Pre-Monsoon Maintenance Work | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31191 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
143 | OCC_236 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31337 | Sd may be availed subject to the availability of 400kV Biswanath Chariali - Balipara 1,2 and 3
144 | OCC_236 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | POWERGRID | D | AR in Non -Auto mode reuqired for Insulator replacment works in 400 KV Balipara - BNC -4 | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31338 | Sd may be availed
145 | OCC_236 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31341 | SD may be availed subject to the availability of 400kV PK bari - Silchar 1, 400kV Palatana-SM Nagar-PK Bari link and 400kV Palatana_silchar link.
146 | OCC_236 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | POWERGRID | D | AR in Non -Auto mode reuqired for Insulator replacment works in 400 KV Silcahr - PK Bari -2 | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31342 | SD may be availed
147 | OCC_236 | POWERGRID | TIE BAY () OF 400KV/220KV BALIPARA-ICT-1 AND BALIPARA - 400KV B/R 1 @BALIPARA - 400KV | POWERGRID | D | AMP works | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31394 | Sd may be availed subject to no outage of element
148 | OCC_236 | POWERGRID | 220 KV MISA 2 BAY AT SAMAGURI | POWERGRID | C | For CB Mechanism overhauling. (Line may be charged through TBC bay. Same may be confirmed with AEGCL in OCC meeting) | 09/Apr/2026 | 09:00 | 11/Apr/2026 | 16:00 |  | RQ31402 | Sd may be aviled subject to no outage of elements.
149 | OCC_236 | AEGCL | 132KV-AGIA-NANGALBIBRA-1 | MEPTCL | D | ROUTINE TESTING | 09/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31272 | S/D may be availed Subject to the availability of 132kV Mendipathar-Agia, 132kV Mendipathar-Nangalbibra. Consent from Meghalaya
150 | OCC_236 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 229 TO 235 | 09/Apr/2026 | 08:30 | 09/Apr/2026 | 16:30 | AGM SARUSAJAI | RQ31303 | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
151 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 09/Apr/2026 | 08:00 | 09/Apr/2026 | 16:00 |  | RQ31351 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
152 | OCC_236 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 314 TO 238 | 09/Apr/2026 | 06:00 | 09/Apr/2026 | 16:00 | AGM SAMAGURI | RQ31305 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
153 | OCC_236 | NEEPCO | AGBPP - GTG 6 | NEEPCO | C | For servicing ,overhauling of L&T make 415V Ckt Bkrs of MCC panel | 23/Apr/2026 | 00:00 | 24/Apr/2026 | 23:59 | Continuous shut down | RQ31178 | SD may be availed. Consent of benefificary is required
154 | OCC_236 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | Tightening of nuts and bolts between Tower Location 130 to 128. | 08/Apr/2026 | 10:00 | 08/Apr/2026 | 15:00 | Avail | RQ31199 | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
155 | OCC_236 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 259 TO 265 | 08/Apr/2026 | 10:00 | 08/Apr/2026 | 16:00 | RE DULLAVCHERRA & AGM PNG | RQ31314 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
156 | OCC_236 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | AEGCL | D | CORRIDOR CLEANING LOC 42 TO 82 | 08/Apr/2026 | 10:00 | 08/Apr/2026 | 16:00 | AGM TINSUKIA | RQ31316 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
157 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31189 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
158 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31190 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
159 | OCC_236 | TSECL | SURAJMANI NAGAR - 132KV - BUS 2 | TSECL | D | Pre-Monsoon Maintenance Work | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31243 | Sd may be availed subject to no outage of elements. All element shifted to Main Bus 1 online before taking SD. 132kV PK Bari(ISTS)-PK Bari, 132kV Surajmaningar(ISTS)-Surajmaningar, 132kV Surajmaningar(ISTS)- Budhjungnagar line must be in service. Intiamtion to NLDC
160 | OCC_236 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31336 | Sd may be availed subject to the availability of 400kV Biswanath Chariali - Balipara 1,2 and 4
161 | OCC_236 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-4 | POWERGRID | D | AR in Non -Auto mode reuqired for Insulator replacment works in 400 KV Balipara - BNC -3 | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31339 | Sd may be availed
162 | OCC_236 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31340 | SD may be availed subject to the availability of 400kV PK bari - Silchar 2, 400kV Palatana-SM Nagar-PK Bari link and 400kV Palatana_silchar link.
163 | OCC_236 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | POWERGRID | D | AR in Non -Auto mode reuqired for Insulator replacment works in 400 KV Silcahr - PK Bari -1 | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31343 | SD may be availed
164 | OCC_236 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | AEGCL | D | CORRIDOR CLEANING | 01/Apr/2026 | 9:00 | 01/Apr/2026 | 16:00 | RE GOLAGHAT | RQ31271 | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
165 | OCC_236 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | AEGCL | D | CORRIDOR CLEANING | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 | RE GOLAGHAT | RQ31290 | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
166 | OCC_236 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | PREVENTIVE MAINTENANCE | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 | RE PAILAPOOL | RQ31293 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
167 | OCC_236 | AEGCL | 132KV-AGIA-MENDIPATHER-1 | MEPTCL | D | ROUTINE TESTING | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31312 | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra.
168 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | NAGALAND,DOP | C | Replacement of 1 no. of Spring Drive for 132kV GIS Ganz make Circuit Breaker Mechanism for Kohima Bay | 08/Apr/2026 | 08:00 | 10/Apr/2026 | 17:00 |  | RQ31320 | SD deferred
169 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 08/Apr/2026 | 08:00 | 08/Apr/2026 | 16:00 |  | RQ31350 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
170 | OCC_236 | AEGCL | 132KV-GOHPUR-NALKATA-2 | POWERGRID | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 101 TO 175 | 08/Apr/2026 | 08:00 | 08/Apr/2026 | 15:00 | AGM NORTH LAKHIMPUR T&T | RQ31284 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
171 | OCC_236 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 08/Apr/2026 | 08:00 | 08/Apr/2026 | 16:00 | AGM NAGAON T&T & AGM MNI | RQ31310 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
172 | OCC_236 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance work | 08/Apr/2026 | 08:00 | 08/Apr/2026 | 16:00 | Avail | RQ31207 | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
173 | OCC_236 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance work | 01/Apr/2026 | 8:00 | 01/Apr/2026 | 16:00 | Avail | RQ31209 | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
174 | OCC_236 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | POWERGRID | D | For attending hotspot from strung bus to R&B Ph CT. | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 14:00 |  | RQ31325 | Sd may be availed. NLDC consent is required
175 | OCC_236 | POWERGRID | SALAKATI - 132KV - BUS 1 | POWERGRID | D | Hotspot attending works in Bus isolator | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 14:00 |  | RQ31405 | Sd may be availed. NLDC consent is required
176 | OCC_236 | POWERGRID | 220KV/132KV SALAKATI-ICT-1 | POWERGRID | D | Hotspot rectfication in Bus isolator at Salakati SS | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 14:00 |  | RQ31407 | SD may be availed
177 | OCC_236 | POWERGRID | 220KV/132KV SALAKATI-ICT-2 | POWERGRID | D | Hotspot rectfication in Bus isolator at Salakati SS | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 14:00 |  | RQ31408 | SD may be availed
178 | OCC_236 | POWERGRID | 220KV/132KV SALAKATI-ICT-3 | POWERGRID | D | Hotspot rectfication in Bus isolator at Salakati SS | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 14:00 |  | RQ31410 | SD may be availed
179 | OCC_236 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 251 TO 258 | 07/Apr/2026 | 10:00 | 07/Apr/2026 | 16:00 | RE DULLAVCHERRA & AGM PNG | RQ31313 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
180 | OCC_236 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 07/Apr/2026 | 09:30 | 07/Apr/2026 | 16:00 | AGM PANCHGRAM | RQ31286 | S/D may be availed.132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. The availability of generation from Leshka will support real-time grid operation during shutdown period. Consented from Assam.
181 | OCC_236 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 07/Apr/2026 | 09:00 | 07/Apr/2026 | 16:00 |  | RQ31188 | S/D may be availed subject to availability of 132kV Monarchak-Palatana-Udaipur. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown.
182 | OCC_236 | POWERGRID | 400KV/132KV BISWANATH CHARIALI-ICT-2 | POWERGRID | D | AMP works | 07/Apr/2026 | 09:00 | 07/Apr/2026 | 16:00 |  | RQ31411 | Sd may be availed subject to the availability of 400/132kV ICT1 at BNC, 132kV Ranganadi-Lekhi, 132kV Ranaganadi-Pare, 132kV Ranganadi-Chimpu-BNC link,
183 | OCC_236 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 07/Apr/2026 | 09:00 | 07/Apr/2026 | 16:00 | RE BOKAJAN | RQ31291 | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
184 | OCC_236 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING LOC 235 TO 247 | 07/Apr/2026 | 08:30 | 07/Apr/2026 | 16:30 | AGM T&T GOALPARA | RQ31301 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
185 | OCC_236 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | MEPTCL | D | Jungle cutting at T/Loc 237 to 245 | 07/Apr/2026 | 08:00 | 07/Apr/2026 | 14:00 | Avail | RQ31197 | S/D may be availed Subject to the availability of 132kV Mendipathar-Agia, 132kV Mendipathar-Nangalbibra. Consent from Assam
186 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 07/Apr/2026 | 08:00 | 07/Apr/2026 | 16:00 |  | RQ31349 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
187 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 07/Apr/2026 | 08:00 | 07/Apr/2026 | 16:00 |  | RQ31357 | SD may be availed subject to availability of 1320kV Doyang-Diampur-II ckt. Intimation to NEEPCO
188 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | AR in Non -auto mode needed For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations in 132 KV Dimapur - Doyang Ckt -1 | 07/Apr/2026 | 08:00 | 07/Apr/2026 | 16:00 |  | RQ31363 | SD may be availed
189 | OCC_236 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE & CORRIDOR CLEANING LOC 101 TO 175 | 07/Apr/2026 | 08:00 | 07/Apr/2026 | 15:00 | AGM NORTH LAKHIMPUR T&T | RQ31282 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
190 | OCC_236 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 06/Apr/2026 | 09:30 | 06/Apr/2026 | 16:30 | AGM PANCHGRAM | RQ31281 | SD May be availed subject to availability of 132 kV Panchgram - Lumshnong, 132 kV Panchgram - Badarpur.
191 | OCC_236 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | NEEPCO | D | Installation of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 06/Apr/2026 | 09:00 | 06/Apr/2026 | 15:00 | Daytime Shutdown of Ranganadi SST-II Transformer is required on 06.04.2026 from 09:00 Hrs to 15:00 Hrs on a daily basis. | RQ31176 | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor
192 | OCC_236 | POWERGRID | 400 KV BISWANATH CHARIALI 2 MAIN BAY(WITH 50 MVAR LINE REACTOR)(407) AT BALIPARA | POWERGRID | D | AMP works | 06/Apr/2026 | 09:00 | 06/Apr/2026 | 16:00 |  | RQ31392 | Sd may be availed subject to no outage of elements
193 | OCC_236 | POWERGRID | TIE BAY () OF 400KV-BALIPARA-BONGAIGAON-3 AND 400KV-AZARA-BONGAIGAON-1 @BONGAIGAON - 400KV | POWERGRID | C | CB mechnism overhualing | 06/Apr/2026 | 09:00 | 09/Apr/2026 | 16:00 |  | RQ31393 | Sd may be availed subject to no outage of elements
194 | OCC_236 | POWERGRID | 220 KV MISA 1 BAY AT SAMAGURI | POWERGRID | C | For CB Mechanism overhauling. (Line may be charged through TBC bay. Same may be confirmed with AEGCL in OCC meeting) | 06/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 |  | RQ31401 | Sd may be availed subject to no outage of elements
195 | OCC_236 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 06/Apr/2026 | 09:00 | 06/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31299 | S/D may be availed. 220 kV Mirza - Boko line and 220 kV Agia - Mirza line to be kept in service.
196 | OCC_236 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 06/Apr/2026 | 09:00 | 06/Apr/2026 | 16:00 |  | RQ31187 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown.
197 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 06/Apr/2026 | 08:00 | 06/Apr/2026 | 16:00 |  | RQ31348 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
198 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 06/Apr/2026 | 08:00 | 06/Apr/2026 | 16:00 |  | RQ31356 | SD may be availed subject to availability of 1320kV Doyang-Diampur-II ckt. Intimation to NEEPCO
199 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | AR in Non -auto mode needed For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations in 132 KV Dimapur - Doyang Ckt -1 | 06/Apr/2026 | 08:00 | 06/Apr/2026 | 16:00 |  | RQ31362 | SD may be availed
200 | OCC_236 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 06/Apr/2026 | 08:00 | 06/Apr/2026 | 16:00 | AGM MARIANI | RQ31267 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
201 | OCC_236 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | LINE MAINTENANCE & CORRIDOR CLEANING | 06/Apr/2026 | 08:00 | 06/Apr/2026 | 16:00 | AGM NAGAON T&T & AGM MNI | RQ31309 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
202 | OCC_236 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 314 TO 238 | 06/Apr/2026 | 06:00 | 06/Apr/2026 | 16:00 | AGM SAMAGURI | RQ31279 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
203 | OCC_236 | NEEPCO | AGBPP - GTG 5 | NEEPCO | C | For servicing ,overhauling of L&T make 415V Ckt Bkrs of MCC panel | 20/Apr/2026 | 00:00 | 21/Apr/2026 | 23:59 | Continuous shut down | RQ31177 | Sd may be availed. Consent from beneificiary is required.
204 | OCC_236 | TSECL | DHARMANAGAR (MISSION TILLA) - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 05/Apr/2026 | 09:00 | 05/Apr/2026 | 16:00 |  | RQ31242 | Sd may be availed subject to the availability of 132kV Hailakandi-Dullavcherra link. Intimation to Assam is required.
205 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 05/Apr/2026 | 09:00 | 05/Apr/2026 | 16:00 |  | RQ31366 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
206 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | AR in Non auto mode required for saver clamp installation 220 kV Balipara-Sonabil -1 | 05/Apr/2026 | 09:00 | 05/Apr/2026 | 16:00 |  | RQ31373 | Sd may be availed
207 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 05/Apr/2026 | 09:00 | 05/Apr/2026 | 16:00 |  | RQ31185 | Sd may be availed subject to the availability of 132kV Hailakandi-Dullavcherra link. Intimation to Assam is required.
208 | OCC_236 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 05/Apr/2026 | 09:00 | 05/Apr/2026 | 16:00 |  | RQ31186 | Sd may be availed subject to the availability of 132kV Hailakandi-Dullavcherra link. Intimation to Assam is required.
209 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 05/Apr/2026 | 08:00 | 05/Apr/2026 | 16:00 |  | RQ31347 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
210 | OCC_236 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | AEGCL | D | CORRIDOR CLEANING LOC 81 TO 159 | 04/Apr/2026 | 09:30 | 04/Apr/2026 | 16:00 | RE RUPAI | RQ31265 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
211 | OCC_236 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 04/Apr/2026 | 09:30 | 04/Apr/2026 | 16:00 | AGM PANCHGRAM | RQ31288 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
212 | OCC_236 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1(Section I) | TSECL | D | Pre-Monsoon Maintenance Work | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 | 132kV Agartala Bus I (Section I) | RQ31241 | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
213 | OCC_236 | POWERGRID | 132KV-MELRIAT-SINHMUI-2 | POWERGRID | D | AMP works | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 17:00 |  | RQ31324 | SD deferred
214 | OCC_236 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31330 | SD may be availed subject to availability of 220kV Misa-Diampur-I ckt.
215 | OCC_236 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-1 | POWERGRID | D | AR in Non -auto mode required for insulator replacment works in 220 Misa - Dimapur - 2 | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31331 | SD may be availed
216 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31365 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
217 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | AR in Non auto mode required for saver clamp installation 220 kV Balipara-Sonabil -1 | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31372 | Sd may be availed
218 | OCC_236 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 08/Apr/2026 | 09:00 | 08/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31297 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
219 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31182 | S/D may be availed 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
220 | OCC_236 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Pre-Monsoon Maintenance Work | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31183 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
221 | OCC_236 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 04/Apr/2026 | 09:00 | 04/Apr/2026 | 16:00 |  | RQ31184 | Sd may be availed subject to the avavilability of 132kV Badarpur-karimganj-kumarghat-Agartala(RC Nagar) link
222 | OCC_236 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA in transmission line | 04/Apr/2026 | 08:00 | 04/Apr/2026 | 16:00 |  | RQ31346 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Annexure B7 to be submitted to NERLDC FTC before charging of element. Consent from Mizoram is required
223 | OCC_236 | POWERGRID | 132KV/33KV ZIRO-ICT-1 | POWERGRID | D | NIFPS servicing works in ICT | 25/Apr/2026 | 7:00 | 25/Apr/2026 | 16:00 |  | RQ31409 | SD may be availed. Consented from AP
224 | OCC_236 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | MEPTCL | D | Jungle cutting at T/Loc 153 to 155 and 157 to 159 | 04/Apr/2026 | 08:00 | 04/Apr/2026 | 13:00 | Avail | RQ31196 | S/D may be availed Subject to the availability of 132kV Mendipathar-Agia, 132kV Mendipathar-Nangalbibra. Consent from Assam
225 | OCC_236 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | NEEPCO | D | Dismantling of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer(SST-II) SSB-C | 03/Apr/2026 | 09:00 | 03/Apr/2026 | 15:00 | Daytime Shutdown of Ranganadi SST-II Transformer is required on 03.04.2026 from 09:00 Hrs to 15:00 Hrs on a daily basis. | RQ31175 | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor
226 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 03/Apr/2026 | 09:00 | 03/Apr/2026 | 16:00 |  | RQ31364 | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
227 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | AR in Non auto mode required for saver clamp installation 220 kV Balipara-Sonabil -1 | 03/Apr/2026 | 09:00 | 03/Apr/2026 | 16:00 |  | RQ31371 | Sd may be availed
228 | OCC_236 | POWERGRID | BUS COUPLER BAY () OF BONGAIGAON(PG) - 220KV - BUS 1 AND BONGAIGAON(PG) - 220KV - BUS 2 @BONGAIGAON - 220KV | POWERGRID | D | AMP works | 03/Apr/2026 | 09:00 | 03/Apr/2026 | 16:00 |  | RQ31391 | Sd may be availed.
229 | OCC_236 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 02/Apr/2026 | 09:30 | 02/Apr/2026 | 16:00 | AGM PANCHGRAM | RQ31287 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
230 | OCC_236 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | POWERGRID | D | AMP works | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31323 | SD may be availed subject to availability of 132 kV Melriat-Sinhmui-II. Consent from Mizoram
231 | OCC_236 | POWERGRID | 220KV-MISA-KOPILI-3 | POWERGRID | D | AMP works | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31333 | SD may be availed subject to the availability of 220kV Misa-Kopili Ckt 1 and 2
232 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31368 | Sd may be availed subject to the availability of 220kV Balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
233 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | AR in Non auto mode required for saver clamp installation 220 kV Balipara-Sonabil -2 | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31370 | Sd may be availed
234 | OCC_236 | POWERGRID | 400KV/220KV MARIANI (PG)-ICT-1 | POWERGRID | D | AMP works | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31412 | Sd may be availed subject to availability of 400/220kV Mariani(PG) ICT-2
235 | OCC_236 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 06/Apr/2026 | 9:00 | 06/Apr/2026 | 16:00 | AGM T&T GOALPARA | RQ31295 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
236 | OCC_236 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Pre-Monsoon Maintenance Work | 02/Apr/2026 | 09:00 | 02/Apr/2026 | 16:00 |  | RQ31181 | SD may be not be allowed due to SD of 132kV SM nagar-Bodhjungnagar line.
237 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 02/Apr/2026 | 08:00 | 02/Apr/2026 | 16:00 |  | RQ31359 | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-1. Intimation to NEEPCO
238 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | AR in Non - Auto mode needed For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations in 132 KV Dimapur - Doyang Ckt -2 | 02/Apr/2026 | 08:00 | 02/Apr/2026 | 16:00 |  | RQ31361 | SD may be availed
239 | OCC_236 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 02/Apr/2026 | 08:00 | 02/Apr/2026 | 16:00 | AGM MARIANI | RQ31266 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
240 | OCC_236 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 82 | 01/Apr/2026 | 10:00 | 01/Apr/2026 | 16:00 | AGM TINSUKIA | RQ31317 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
241 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 |  | RQ31367 | Sd may be availed subject to the availability of 220kV Balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
242 | OCC_236 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | AR in Non auto mode required for saver clamp installation 220 kV Balipara-Sonabil -2 | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 |  | RQ31369 | Sd may be availed
243 | OCC_236 | POWERGRID | TIE BAY () OF 400KV-BISWANATH CHARIALI-BALIPARA-1 AND 400KV-BALIPARA-MISA-1 @BALIPARA - 400KV | POWERGRID | D | AMP works | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 |  | RQ31390 | SD may be availed subject to no outage of elements
244 | OCC_236 | POWERGRID | ROING - 132KV B/R 1 | POWERGRID | D | AMP Works | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 |  | RQ31413 | SD may be availed
245 | OCC_236 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | PREVENTIVE MAINTENANCE | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 | RE PAILAPOOL | RQ31292 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
246 | OCC_236 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 01/Apr/2026 | 09:00 | 01/Apr/2026 | 16:00 |  | RQ31179 | S/D may be availed subject to availability of 132kV Monarchak-Palatana-Udaipur. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown.
247 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 01/Apr/2026 | 08:00 | 01/Apr/2026 | 16:00 |  | RQ31358 | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-1. Intimation to NEEPCO
248 | OCC_236 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | AR in Non - Auto mode needed For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations in 132 KV Dimapur - Doyang Ckt -2 | 01/Apr/2026 | 08:00 | 01/Apr/2026 | 16:00 |  | RQ31360 | SD may be availed