## Sheet1
Sl. no | occ number | Name of requesting agency | Element name | owner | daily/ continous | Reason | Shutdown start date | Shutdown start time | Shutdown end date | Shutdown end time | requester remarks | tag | reference number | Study comments
202 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 01/May/2026 | 09:00 | 01/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31627 | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
33 | OCC_237 | NEEPCO | 132KV/33KV RANGANADI-ICT-1 | NEEPCO | D | Installation of new ABT Management System on SST-I Panel in Control Room | 01/May/2026 | 09:00 | 01/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31807 | SD may be availed subject to availability of 132/33kV SST-2 at Panyor
142 | OCC_237 | POWERGRID | 132KV-BISWANATH CHARIALI-PAVOI-1 | POWERGRID | D | AMP works | 01/May/2026 | 09:00 | 01/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31691 | SD may be availed subject to availability of 132kV BNC - Pavoi-2, 132kV BNC - gohpur - Pavoi link
254 | OCC_237 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 01/May/2026 | 09:00 | 01/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31580 | SD May be availed subject to availability of 132 kV Panchgram - Lumshnong & 132 kV Panchgram - Badarpur.
76 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI II & 400 KV MISA II (408)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 02/May/2026 | 08:00 | 02/May/2026 | 21:00 |  | R&U works Related Shut Down under PSDF | RQ31758 | Sd deferred
140 | OCC_237 | POWERGRID | 400KV-IMPHAL(PG)-THOUBAL-2 | MSPCL | D | OPGW Stringing in between location no T-482(DA-1.5) of 400 kv Silchar-Imphal Ckt-1 to location no T-4/1(DA-1.5) of 400 kV Imphal-Thoubal Ckt-2.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 02/May/2026 | 08:00 | 02/May/2026 | 16:00 |  | Contruction | RQ31692 | SD may be availed subject to availability of 132kV Imphal – Yingagangpokpi-Kongba-New Thoubal – Old Thoubal – Kakching – Churachandpur – Ningthoukhong link. Manipur demand to be kept below 170 MW to avoid low voltage under n-1 contingecy of 132kV Ningthoukhong – Churachandpur II. Manipur consent is required.
141 | OCC_237 | POWERGRID | 132KV-IMPHAL(PG)-SILCHAR-1 | POWERGRID | D | OPGW Stringing in between location no T-482(DA-1.5) of 400 kv Silchar-Imphal Ckt-1 to location no T-4/1(DA-1.5) of 400 kV Imphal-Thoubal Ckt-2.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 02/May/2026 | 08:00 | 02/May/2026 | 16:00 |  | Contruction | RQ31693 | Sd deferred
274 | OCC_237 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 1 TO 25 | 02/May/2026 | 10:00 | 02/May/2026 | 14:00 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31610 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
275 | OCC_237 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 1 TO 75 | 02/May/2026 | 09:00 | 02/May/2026 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | RQ31556 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
75 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI I & 400 KV MISA I (411)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 02/May/2026 | 08:00 | 02/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31757 | Sd deferred
269 | OCC_237 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | CONDUCTOR RESTRINGING IN BETWEEN LOC 160 & 165 | 02/May/2026 | 09:00 | 02/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31570 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
143 | OCC_237 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | MSPCL | C | Monthly change of 3*105MVA transfer (Y,B&sphare will be charged) | 02/May/2026 | 11:30 | 02/May/2026 | 13:30 | No load will be affected | Existing System Normal Maintenance Related Shut Down | RQ31689 | SD may be availed subject to the Imphal-Yurembam-Yiangangpopki-Kongba-Thubal-kakching-Churachandpur-Ningthoukhong link.
27 | OCC_237 | NEEPCO | 400KV/132KV RANGANADI-ICT-2 | NEEPCO | D | Installation of new ABT Management System on 132 kV Side ICT-II Panel in Control Room | 02/May/2026 | 09:00 | 02/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31813 | Sd may be availed subject to the availability of 400/132kV ICT-1 at Panyor, 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link.
32 | OCC_237 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | NEEPCO | D | Installation of new ABT Management System on SST-II Panel in Control Room | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31808 | SD May be availed subject to availability of 132/33kV ICT-2 at Panyor
138 | OCC_237 | POWERGRID | 400KV-IMPHAL(PG)-NEW KOHIMA-1 | KMTL | D | OPGW Stringing in between location no T-482(DA-1.5) of 400 kv Silchar-Imphal Ckt-2 to location no T-5/0(DD+6) of 400 kV Imphal-New Kohima Ckt-1.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 03/May/2026 | 08:00 | 03/May/2026 | 16:00 |  | Contruction | RQ31694 | S/D may be availed subject to the availability of 400kV Imphal - New Kohima 2 and 400kV Silchar - Imphal D/C. 125 MVAR BR at 400kV Imphal and one 125 MVAR BR 400kV New Kohima S/S to be opened before availing shutdown
139 | OCC_237 | POWERGRID | 132KV-IMPHAL(PG)-SILCHAR-2 | POWERGRID | D | OPGW Stringing in between location no T-482(DA-1.5) of 400 kv Silchar-Imphal Ckt-2 to location no T-5/0(DD+6) of 400 kV Imphal-New Kohima Ckt-1.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 03/May/2026 | 08:00 | 03/May/2026 | 16:00 |  | Contruction | RQ31695 | Sd deferred
150 | OCC_237 | TSECL | P K BARI - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31679 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra, 132kV Agartala-AGTCCPP D/C, 132kV Agartala-Mohanpur-Dhalabil-Kamalpur link, Agaratala-Suramaningar-Surajmaninagar(ISTS)-PK bari-Silchar link. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period.
195 | OCC_237 | TSECL | 132KV-AGTCCPP-P K BARI-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31628 | SD may be availed
196 | OCC_237 | TSECL | 132KV-AGTCCPP-P K BARI-2 | INDIGRID | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31629 | SD may be availed
197 | OCC_237 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31630 | S/D may be availed
198 | OCC_237 | TSECL | 132KV-KAILASOHAR-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31631 | SD may be availed
199 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31632 | SD may be availed
200 | OCC_237 | TSECL | 132KV-KAMALPUR-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31633 | SD may be availed
201 | OCC_237 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 03/May/2026 | 09:00 | 03/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31634 | SD may be availed
31 | OCC_237 | NEEPCO | RANGANADI - UNIT 1 | NEEPCO | D | Installation of new ABT Management System on Unit-I Panel in Control Room | 04/May/2026 | 09:00 | 04/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31809 | SD may be availed. In case of spillage or high water level, shutdown will be deffered.
70 | OCC_237 | POWERGRID | MAIN BAY (202) OF 400KV/220KV BALIPARA-ICT-1 @BALIPARA - 220KV | POWERGRID | D | AMP OF MAIN BAY EQUIPMENT, ICT SHALL BE IN SERVICE. | 04/May/2026 | 09:00 | 04/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31759 | SD may be availed subject to outage of elements. ICT-1 may be charged through transfer bus.
73 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI I & 400 KV MISA I (411)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 04/May/2026 | 08:00 | 04/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31760 | Sd deferred
74 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI II & 400 KV MISA II (408)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 04/May/2026 | 08:00 | 04/May/2026 | 21:00 |  | R&U works Related Shut Down under PSDF | RQ31762 | Sd deferred
135 | OCC_237 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | POWERGRID | D | For testing & commissioning of 03 nos. 132KV Line CVT in PG Incoming#1 bay at Sihhmui SS | 04/May/2026 | 08:00 | 04/May/2026 | 16:00 |  | Contruction | RQ31696 | SD may be availed subject to availability of 132kV Melriat - Simuii II
136 | OCC_237 | POWERGRID | 400KV-IMPHAL(PG)-NEW KOHIMA-2 | KMTL | D | OPGW Stringing in between location no T-9/0(D+6) of 132 kv Loktak-Imphal Line to location no T-5/0(DD+6) of 400 kV Imphal-New Kohima Ckt-2.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 04/May/2026 | 08:00 | 04/May/2026 | 16:00 |  | Contruction | RQ31697 | S/D may be availed subject to the availability of 400kV Imphal - New Kohima 1 and 400kV Silchar - Imphal D/C. 125 MVAR BR at 400kV Imphal and one 125 MVAR BR 400kV New Kohima S/S to be opened before availing shutdown
137 | OCC_237 | POWERGRID | 132KV-IMPHAL-LOKTAK-1 | POWERGRID | D | OPGW Stringing in between location no T-9/0(D+6) of 132 kv Loktak-Imphal Line to location no T-5/0(DD+6) of 400 kV Imphal-New Kohima Ckt-2.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 04/May/2026 | 08:00 | 04/May/2026 | 16:00 |  | Contruction | RQ31698 | SD may be availed subject to availability of 132kV Loktak – Jiribam(PG) and 132kV Loktak – Ningthoukhong. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period.
193 | OCC_237 | TSECL | 132KV-AMBASA-MANU-1 | TSECL | D | Pre-Monsoon Maintenance Work | 04/May/2026 | 09:00 | 04/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31636 | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
194 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Pre-Monsoon Maintenance Work | 04/May/2026 | 09:00 | 04/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31635 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 1 needs to be under 70MW.
272 | OCC_237 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/May/2026 | 09:30 | 04/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31589 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
273 | OCC_237 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | CONDUCTOR RESTRINGING IN BETWEEN LOC 160 & 165 | 04/May/2026 | 09:00 | 04/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31569 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
72 | OCC_237 | POWERGRID | MAIN BAY () OF 400KV-BISWANATH CHARIALI-SUBANSIRI-3 @BISWANATH CHARIALI - 400KV | POWERGRID | C | Breaker overhauling of 400kV BNC-Lower Subansiri circuit-3 Main bay at BNC | 04/May/2026 | 09:00 | 06/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31763 | Sd may be availed subject to availability of 400kV BNC-LS-3 & 400kV BNC-LS-4 tie bay and 400kV BNC - LS-4 main bay at 400kV BNC S/S
71 | OCC_237 | POWERGRID | 400 KV AZARA BAY AT BONGAIGAON | POWERGRID | C | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 04/May/2026 | 09:00 | 07/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31761 | SD may be availed subject to availability of 400kV Bongaigaon - Balipara III and 400kV Bongaigaon - Mirza tie bay and 400kV Bongaigaon - Balipara III main bay at 400kV Bongaigaon S/S
30 | OCC_237 | NEEPCO | RANGANADI - UNIT 2 | NEEPCO | D | Installation of new ABT Management System on Unit-II Panel in Control Room | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31810 | SD may be availed. In case of spillage or high water level, shutdown will be deffered.
35 | OCC_237 | POWERGRID | 220KV/132KV DIMAPUR (PG)-ICT-3 | POWERGRID | D | Warranty Test for GIS bays at Dimapur SS | 05/May/2026 | 08:00 | 05/May/2026 | 16:00 |  |  | RQ31798 | SD may be availed subject to the availability of 220kV ICT 1 and 2 at Dimapur
43 | OCC_237 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 L/R@ MISA - 400KV | POWERGRID | D | For AMP of Line Reactor. (Line outage is required during isolation and restoration of LR ) | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31790 | SD may be availed
69 | OCC_237 | POWERGRID | 63 MVAR BUS REACTOR 2 BAY AT SILCHAR | POWERGRID | D | AMP Works | 05/May/2026 | 10:00 | 05/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31764 | SD may be availed subjected to availability of 400kV Silchar - Palatana 1 & 63 MVAR BR2 tie bay and 400kV Silchar - Palatana 1 main bay at 400kV Silchar S/S
132 | OCC_237 | POWERGRID | 400KV-IMPHAL(PG)-THOUBAL-1 | MSPCL | D | OPGW Stringing in between location no T-6/0(D+6) of 132 kv loktak line to location no T-4/1(DA+1.5) of 400 kV Imphal-Thoubal line-1 UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 05/May/2026 | 08:00 | 05/May/2026 | 16:00 |  | Contruction | RQ31699 | Since line is already under outage since 18th Oct 2021. The work may be carried out. Intimation to Manipur.
133 | OCC_237 | POWERGRID | 132KV-IMPHAL-LOKTAK-1 | POWERGRID | D | OPGW Stringing in between location no T-6/0(D+6) of 132 kv loktak line under diamond crossings location no T-4/1(DA+1.5) of 400 kV Imphal-Thoubal line-1.UNDER RAILWAY DIVERSION works of Imphal Loktak line under crossings of 400kv lines. There is no outage in the existing link | 05/May/2026 | 08:00 | 05/May/2026 | 16:00 |  | Contruction | RQ31700 | SD may be availed subject to availability of 132kV Loktak – Jiribam(PG) and 132kV Loktak – Ningthoukhong. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period.
191 | OCC_237 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31638 | SD may be availed subject to the availabitiy of 132kV SM Nagar(ISTS) - Budhjungnagar,132kV Agartala - Budhjungnagar, 132kV SM Nagar(ISTS) - SM Nagar, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK bari.
192 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31637 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
268 | OCC_237 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 | AGM DHALIGAON & AGM RNG | R&U works Related Shut Down under PSDF | RQ31565 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
270 | OCC_237 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 42 TO 74 | 05/May/2026 | 08:30 | 05/May/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31576 | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
271 | OCC_237 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/May/2026 | 08:00 | 05/May/2026 | 16:00 | AGM MNI | R&U works Related Shut Down under PSDF | RQ31559 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
8 | OCC_237 | OTPCL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Annual maintenance and testing | 05/May/2026 | 07:00 | 05/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31834 | SD may be availed subject to the availability of 132kV Monarchak - udaipur and 132kV Monarchak - rokhia. Monarchak Generation to kept below 70 MW. SPS at Monarchak may be disabled before avaling shutdown.
259 | OCC_237 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 05/May/2026 | 09:00 | 05/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31598 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service.
29 | OCC_237 | NEEPCO | RANGANADI - UNIT 3 | NEEPCO | D | Installation of new ABT Management System on Unit-III Panel in Control Room | 06/May/2026 | 09:00 | 06/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31811 | SD may be availed. In case of spillage or high water level, shutdown will be deffered.
44 | OCC_237 | POWERGRID | BALIPARA - 400KV B/R 3 | POWERGRID | D | AMP OF BUS REACTOR | 06/May/2026 | 09:00 | 06/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31789 | SD may be availed. Voltage rise of 3-4kV may be observed at Balipara while switching the reactor
34 | OCC_237 | POWERGRID | 220KV/132KV DIMAPUR (PG)-ICT-3 | POWERGRID | D | Warranty Test for GIS bays at Dimapur SS | 06/May/2026 | 08:00 | 06/May/2026 | 16:00 |  |  | RQ31799 | SD may be availed subject to the availability of 220kV ICT 1 and 2 at Dimapur
67 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI I & 400 KV MISA I (411)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 06/May/2026 | 08:00 | 06/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31765 | Sd deferred
68 | OCC_237 | POWERGRID | 400 KV BONGAIGAON I & 400 KV BISWANATH CHARIALI III (414)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 06/May/2026 | 08:00 | 06/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31766 | Sd deferred
128 | OCC_237 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 06/May/2026 | 09:00 | 06/May/2026 | 16:00 |  | Existing System Improvement Related Shut Down | RQ31702 | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 2, 3 and 4.
190 | OCC_237 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 06/May/2026 | 09:00 | 06/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31639 | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link. Monarchak Generation to be kept below 75 MW and SPS of Monarchak to be kept OFF before availing the shutdown
261 | OCC_237 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | AEGCL | D | CORRIDOR CLEANING | 06/May/2026 | 10:00 | 06/May/2026 | 16:00 | AGM TSK | R&U works Related Shut Down under PSDF | RQ31620 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
262 | OCC_237 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | CONDUCTOR RESTRINGING IN BETWEEN LOC 160 & 165 | 06/May/2026 | 09:00 | 06/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31571 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
264 | OCC_237 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/May/2026 | 08:00 | 06/May/2026 | 16:00 | AGM MNI | R&U works Related Shut Down under PSDF | RQ31560 | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
265 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 314 TO 238 | 06/May/2026 | 08:00 | 06/May/2026 | 15:00 | AGM SMG | R&U works Related Shut Down under PSDF | RQ31578 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
266 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE IN LOC 101-149 | 06/May/2026 | 08:00 | 06/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31581 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
130 | OCC_237 | POWERGRID | 132KV-MELRIAT-SINHMUI-2 | POWERGRID | D | For testing & commissioning of 03 nos. 132KV Line CVT in PG Incoming#2 bay at Sihhmui SS | 06/May/2026 | 08:00 | 06/May/2026 | 16:00 |  | Contruction | RQ31701 | Sd may be availed subject to availability of 132kV Melriat - Shimuii I
281 | OCC_237 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance Work | 06/May/2026 | 08:00 | 06/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31547 | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
267 | OCC_237 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | REPLACEMENT OF EXISTING BAY CT WITH NEW UPGRADED ONE | 06/May/2026 | 07:00 | 06/May/2026 | 16:00 | RE PLP | R&U works Related Shut Down under PSDF | RQ31596 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
19 | OCC_237 | OTPCL | 400KV/132KV PALATANA-ICT-2 | OTPC | C | Maintenance and testing of ICT 2 | 06/May/2026 | 07:00 | 09/May/2026 | 16:00 |  |  | RQ31821 | 400/132kV ICT-2 at Palatana may be availed subject to availability of ICT-1. SPS realted to Outage/tripping of both 400/132 kV, 2x125 MVA ICTs at Palatana to be kept ON during the shutdown period if combined demand of Tripura including Bangladesh is more than 460 MW.Dia to be closed at Palatana after availing shutdown.
282 | OCC_237 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance Work | 07/May/2026 | 08:00 | 07/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31548 | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
28 | OCC_237 | NEEPCO | 400KV/132KV RANGANADI-ICT-1 | NEEPCO | D | Installation of new ABT Management System on 132 kV Side ICT-I Panel in Control Room | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31812 | Sd may be availed subject to the availability of 400/132kV ICT 1 and 2 at BNC, BNC-Chimpu-Pare, chimpu-ranganadi link,ranganadi- Ziro-dapo-basar-along-roing link. One machine of Pare to be scheduled during the shutdown period with no machine of Panyor.
42 | OCC_237 | POWERGRID | SILCHAR - 132KV - BUS 2 | POWERGRID | D | AMP WORK AND BUSBAR RELAY TESTING) | 07/May/2026 | 08:00 | 07/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31792 | SD may be availed subject to no outage of elements. All the elements to be transferred to other bus before availing the shutdown. 132kV Aizwal - Melriat line to be in service.
66 | OCC_237 | POWERGRID | BUS COUPLER BAY () OF SILCHAR - 132KV - BUS 1 AND SILCHAR - 132KV - BUS 2 @SILCHAR - 132KV | POWERGRID | D | Busbar Testing works | 07/May/2026 | 08:00 | 07/May/2026 | 17:00 |  |  | RQ31783 | Sd may be availed subject to no outage of elements
188 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31641 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
189 | OCC_237 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31640 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. before final charging of the line
206 | OCC_237 | AEGCL | 400KV/220KV AZARA-ICT-1 | AEGCL | D | ROUTINE BAY MAINTENANCE | 07/May/2026 | 07:00 | 07/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31623 | SD may be availed sibject to availability of 400/220kV ICT 2 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link
256 | OCC_237 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 | AGM DHALIGAON & AGM RNG | R&U works Related Shut Down under PSDF | RQ31567 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
257 | OCC_237 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | CONDUCTOR RESTRINGING IN BETWEEN LOC 160 & 165 | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31572 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
258 | OCC_237 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | AEGCL | D | CORRIDOR CLEANING | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 | RE GLG | R&U works Related Shut Down under PSDF | RQ31594 | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
260 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-2 | POWERGRID | D | LINE MAINTENANCE IN LOC 1-34 | 07/May/2026 | 08:00 | 07/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31584 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & 132kV Nirjuli - North Lakimpur line..
284 | OCC_237 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | MEPTCL | D | Jungle cutting at T/Loc 236-249 and Loc 297-299 | 07/May/2026 | 09:00 | 07/May/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31545 | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra.
125 | OCC_237 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 07/May/2026 | 09:00 | 07/May/2026 | 16:00 |  | Existing System Improvement Related Shut Down | RQ31704 | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 1, 3 and 4
127 | OCC_237 | POWERGRID | 132KV-SILCHAR-BADARPUR-2 | POWERGRID | D | 132 kV BUSBAR TESTTING. | 07/May/2026 | 08:00 | 07/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31703 | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-1
203 | OCC_237 | AEGCL | DULLAVCHERRA - 132KV - BUS 1 | AEGCL | D | PREVENTIVE MAINTENANCE | 07/May/2026 | 06:00 | 07/May/2026 | 10:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31626 | SD may be availed subject to the availability of 132kV PK Bari-Dharmanagar. Consent from Tripura
61 | OCC_237 | POWERGRID | MAIN BAY (205) OF 400KV/220KV BALIPARA-ICT-2 @BALIPARA - 220KV | POWERGRID | D | AMP OF BAY EQUIPMENT. ICT#2 shall be remain charged through TBC Bay . | 08/May/2026 | 09:00 | 08/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31767 | SD may be availed subject to outage of elements. ICT-2 may be charged through transfer bus.
41 | OCC_237 | POWERGRID | SILCHAR - 132KV - BUS 1 | POWERGRID | D | 132 KV MAIN BUS-1 AT SILCHAR SS.(BUSBAR RELAY TESTING) | 08/May/2026 | 08:00 | 08/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31791 | SSD may be availed subject to no outage of elements. All the elements to be transferred to other bus before availing the shutdown. 132kV Aizwal - Melriat line to be in service.
62 | OCC_237 | POWERGRID | BUS COUPLER BAY () OF BONGAIGAON(PG) - 220KV - BUS 1 AND BONGAIGAON(PG) - 220KV - BUS 2 @BONGAIGAON - 220KV | POWERGRID | D | AMP OF BAY EQUIPMENT | 08/May/2026 | 09:00 | 08/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31768 | SD may be availed. Elements to be segretted propoerly in both the buses. Bus 1: Ict-1, Salakati 1 & Bus 2: ICT-2 , Salakati 2
63 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI I & 400 KV MISA I (411)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-2 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 08/May/2026 | 08:00 | 08/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31769 | Sd deferred
64 | OCC_237 | POWERGRID | 400 KV BONGAIGAON I & 400 KV BISWANATH CHARIALI III (414)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 08/May/2026 | 08:00 | 08/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31770 | Sd deferred
124 | OCC_237 | POWERGRID | 132KV-IMPHAL-LOKTAK-1 | POWERGRID | C | For Connection in SPAN 101 to 110 & 114 for diversion work of section 110 to 114 by NF Railway diversion works | 08/May/2026 | 08:00 | 10/May/2026 | 16:00 |  | Contruction | RQ31706 | SD may be availed subject to availability of 132kV Loktak – Jiribam(PG) and 132kV Loktak – Ningthoukhong. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period.
187 | OCC_237 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Pre-Monsoon Maintenance Work | 08/May/2026 | 9:00 | 08/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31642 | SD may be availed subject to the availability of 132kV Sm Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. SD may be allowed only after restoration of 132kV PK Bari - Manu
252 | OCC_237 | AEGCL | 132KV-TINSUKIA-LEDO-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 110 TO 113 | 08/May/2026 | 10:00 | 08/May/2026 | 16:00 | RE LEDO | R&U works Related Shut Down under PSDF | RQ31592 | SD may be availed subject to the availability of 132kV Tinsukia-Rupai -LEDO link and 132kV Roing - Chapakhowa - Rupai link
253 | OCC_237 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | CONDUCTOR RESTRINGING IN BETWEEN LOC 160 & 165 | 08/May/2026 | 09:00 | 08/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31573 | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
255 | OCC_237 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 65 | 08/May/2026 | 08:00 | 08/May/2026 | 16:00 | AGM MNI & AGM NGN T&T | R&U works Related Shut Down under PSDF | RQ31617 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
65 | OCC_237 | POWERGRID | BUS COUPLER BAY () OF SILCHAR - 132KV - BUS 1 AND SILCHAR - 132KV - BUS 2 @SILCHAR - 132KV | POWERGRID | D | Busbar Testing works | 08/May/2026 | 08:00 | 08/May/2026 | 16:00 |  |  | RQ31784 | Sd may be availed subject to no outage of elements
123 | OCC_237 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | POWERGRID | D | 132 kV BUSBAR TESTTING. | 08/May/2026 | 08:00 | 08/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31705 | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2.
38 | OCC_237 | NEEPCO | MONARCHAK(THERMAL) - GTG 1 | NEEPCO | C | GT Inlet air filter replacement, Compressor offline washing, and other electrical maintenance works | 09/May/2026 | 00:00 | 13/May/2026 | 23:59 | Planned Shutdown |  | RQ31794 | Sd deferred
39 | OCC_237 | NEEPCO | MONARCHAK(THERMAL) - UNIT 2 | NEEPCO | C | GT Inlet air filter replacement, Compressor offline washing, and other electrical maintenance works | 09/May/2026 | 00:00 | 13/May/2026 | 23:59 | Planned Shutdown |  | RQ31795 | Sd deferred
149 | OCC_237 | TSECL | BUDHJANGNAGAR - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31680 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
183 | OCC_237 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31645 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari.SD may be availed after charging of 132kV PK Bari-Manu line.
184 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31646 | Sd may be availed subject to the availability of 132kV SM Nagar(ISTS)-Budhjungnagar and 132kV Surajmaninagar(TSECL)-Budhjungnagar. SD may be availed after charging of 132kV PK Bari-Manu line.
185 | OCC_237 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31643 | SD may be availed subject to the availabitiy of 132kV SM Nagar(ISTS) - Budhjungnagar,132kV Agartala - Budhjungnagar, 132kV SM Nagar(ISTS) - SM Nagar and 132kV PK Bari(ISTS) - PK bari. SD may be availed after charging of 132kV PK Bari-Manu line.
186 | OCC_237 | TSECL | 132KV-BODHJUNGNAGAR-JIRANIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31644 | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Line loading of 132 PK Bari-Pk Bari needs to be maintained below 74MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
84 | OCC_237 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | POWERGRID | D | AMP works | 09/May/2026 | 08:00 | 09/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31712 | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh
20 | OCC_237 | NEEPCO | MAIN BAY (GIS) OF BR-1 @RANGANADI - 400KV | NEEPCO | D | Installation of new ABT Management System on 400 kV Bus Reactor Panel in Control Room | 09/May/2026 | 09:00 | 09/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31820 | Sd may be availed.
25 | OCC_237 | NEEPCO | 132 KV ITANAGAR 2 BAY AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 132 kV Side Lekhi Panel in Control Room | 10/May/2026 | 09:00 | 10/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31815 | SD may be availed subject to availability of 132kV Panyor – Itanagar, 132kV Panyor – Pare, 400/132kV ICT 1 at Panyor. One machine of Pare to be scheduled during the shutdown period with no machine of Panyor.
120 | OCC_237 | POWERGRID | 132KV-JIRIBAM (MA)-JIRIBAM(PG)-1 | MSPCL | D | Cleaning of GIS Busduct and Bushing, AMP/Warranty Test of Bay equipments. | 10/May/2026 | 08:00 | 10/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31707 | As 132kV Jiribam - Rengpang is under long outage. During shutdown of 132kV JIribam(PG) - Jiribam, Jiribma area will be under blackout. Manipur consent is required
179 | OCC_237 | TSECL | 132KV-AMBASA-KAMALPUR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 10/May/2026 | 09:00 | 10/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31650 | SD may be availed subject to availability of 132kV Budjungnagar – Jirinia – Gamaitila. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa Bus 132kV Manu S/S will be black out.
16 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-1 | NETC | D | Annual maintenance and testing | 10/May/2026 | 07:00 | 10/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31824 | SD may be availed subject to the availability of 400kV Palatana-Silchar 2, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
18 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-1 L/R@ PALATANA - 400KV | POWERGRID | C | Annual maintenance and testing | 10/May/2026 | 07:00 | 12/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31822 | SD may be availed.
57 | OCC_237 | POWERGRID | MAIN BAY () OF 400KV-BALIPARA-KAMENG-2 @BALIPARA - 400KV | NEEPCO | D | AMP OF BAY EQUIPMENT | 11/May/2026 | 09:00 | 11/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31771 | Sd may be availed subject to availability of 400kV Balipara - Bongaigaon III main bay and 400kV Balipara - Kameng II & 400kV Balipara - Bongaigaon III tie bay at 400kV Balipara S/S
15 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-1 | NETC | D | Annual maintenance and testing | 11/May/2026 | 07:00 | 11/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31825 | SD may be availed subject to the availability of 400kV Palatana-Silchar 2, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
116 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/May/2026 | 08:00 | 11/May/2026 | 16:00 |  |  | RQ31720 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required.
117 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/May/2026 | 08:00 | 11/May/2026 | 16:00 |  |  | RQ31726 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
58 | OCC_237 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | POWERGRID | D | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 11/May/2026 | 09:00 | 11/May/2026 | 17:00 |  |  | RQ31785 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
177 | OCC_237 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 11/May/2026 | 09:00 | 11/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31652 | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link. Monarchak Generation to be kept below 75 MW and SPS of Monarchak to be kept during the shutdown period.
251 | OCC_237 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 11/May/2026 | 09:00 | 11/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31587 | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service.
59 | OCC_237 | POWERGRID | TIE BAY (417) OF 400KV-BALIPARA-BONGAIGAON-2 AND 400KV-BISWANATH CHARIALI-BALIPARA-4 @BALIPARA - 400KV | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-3 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 11/May/2026 | 08:00 | 11/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31772 | Sd deferred
60 | OCC_237 | POWERGRID | 400 KV BONGAIGAON I & 400 KV BISWANATH CHARIALI III (414)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 11/May/2026 | 08:00 | 11/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31773 | Sd deferred
118 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 11/May/2026 | 08:00 | 11/May/2026 | 16:00 |  |  | RQ31732 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
23 | OCC_237 | NEEPCO | 132 KV ITANAGAR I BAY AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 132 kV Side Chimpu Panel in Control Room | 12/May/2026 | 09:00 | 12/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31817 | SD may be availed subject to availability of 132kV Panyor – Pare, 132kV Panyor – Lekhi, 400/132kV ICT 1&2 at Panyor. One machine of Pare to be scheduled during the shutdown period with no machine of Panyor.
112 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 12/May/2026 | 08:00 | 12/May/2026 | 16:00 |  |  | RQ31721 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required.
113 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 12/May/2026 | 08:00 | 12/May/2026 | 16:00 |  |  | RQ31727 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
175 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/May/2026 | 09:00 | 12/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31654 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
176 | OCC_237 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 12/May/2026 | 09:00 | 12/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31653 | SD may be availed subject to availability of 132kV Badarpur - Karmaganj-Kumrghat link, 132kV AGTCCPP - Kumarghat and 132kV Kumarghat - Aizwal
205 | OCC_237 | AEGCL | 400KV/220KV AZARA-ICT-2 | AEGCL | D | ROUTINE BAY MAINTENANCE | 12/May/2026 | 07:00 | 12/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31624 | SD may be availed sibject to availability of 400/220kV ICT 1 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link
248 | OCC_237 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 12/May/2026 | 09:00 | 12/May/2026 | 16:00 | AGM DHALIGAON & AGM RNG | R&U works Related Shut Down under PSDF | RQ31566 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
249 | OCC_237 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 12/May/2026 | 09:00 | 12/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31588 | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service.
250 | OCC_237 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 66 TO 135 | 12/May/2026 | 08:00 | 12/May/2026 | 16:00 | AGM MNI & AGM NGN T&T | R&U works Related Shut Down under PSDF | RQ31618 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
287 | OCC_237 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 124 to 122. | 12/May/2026 | 10:00 | 12/May/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31542 | SD may be availed
14 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-1 | NETC | D | Annual maintenance and testing | 12/May/2026 | 07:00 | 12/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31826 | SD may be availed subject to the availability of 400kV Palatana-Silchar 2, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
37 | OCC_237 | POWERGRID | 220KV/132KV DIMAPUR-ICT-1 | POWERGRID | D | Warranty Test for GIS bays at Dimapur SS | 12/May/2026 | 08:00 | 12/May/2026 | 16:00 |  |  | RQ31796 | SD may be availed subject to availability 220/132kV ICT-2 & ICT-3 at Dimapur and 132kV Dimapur – Imphal line.
56 | OCC_237 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | POWERGRID | D | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 12/May/2026 | 09:00 | 12/May/2026 | 17:00 |  |  | RQ31786 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
114 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 12/May/2026 | 08:00 | 12/May/2026 | 16:00 |  |  | RQ31733 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
22 | OCC_237 | NEEPCO | 400 KV BNC 1 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 400 kV BNC-I and Line Reactor-I Panel in Control Room | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31818 | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 2 as N-1 contigency, Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
13 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-2 | NETC | D | Annual maintenance and testing | 13/May/2026 | 07:00 | 13/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31827 | SD may be availed subject to the availability of 400kV Palatana-Silchar 1, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
36 | OCC_237 | POWERGRID | 220KV/132KV DIMAPUR-ICT-1 | POWERGRID | D | Warranty Test for GIS bays at Dimapur SS | 13/May/2026 | 08:00 | 13/May/2026 | 16:00 |  |  | RQ31797 | SD may be availed subject to availability 220/132kV ICT-2 & ICT-3 at Dimapur and 132kV Dimapur – Imphal line.
52 | OCC_237 | POWERGRID | 400 KV, 315 MVA ICT 3 MAIN BAY AT SILCHAR | POWERGRID | D | AMP Works | 13/May/2026 | 10:00 | 13/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31774 | Sd may availed subject to availability of other main bay of ICT-3 at 400kV Silchar S?S
53 | OCC_237 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | POWERGRID | D | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 13/May/2026 | 09:00 | 13/May/2026 | 17:00 |  |  | RQ31787 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
108 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/May/2026 | 08:00 | 13/May/2026 | 16:00 |  |  | RQ31722 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required.
109 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/May/2026 | 08:00 | 13/May/2026 | 16:00 |  |  | RQ31728 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
54 | OCC_237 | POWERGRID | TIE BAY (417) OF 400KV-BALIPARA-BONGAIGAON-2 AND 400KV-BISWANATH CHARIALI-BALIPARA-4 @BALIPARA - 400KV | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-3 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 13/May/2026 | 08:00 | 13/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31775 | Sd deferred
174 | OCC_237 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31655 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar. Monarchak Generation to be available. Combined loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW during the shutdown period.
244 | OCC_237 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | C | LINE MAINTENANCE & corridor cleaning | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31574 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
245 | OCC_237 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 | RE BKJ | R&U works Related Shut Down under PSDF | RQ31595 | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
246 | OCC_237 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31602 | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
247 | OCC_237 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE AT LOC 314 TO 238 | 13/May/2026 | 08:00 | 13/May/2026 | 15:00 | AGM SMG | R&U works Related Shut Down under PSDF | RQ31611 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
55 | OCC_237 | POWERGRID | 400 KV BONGAIGAON I & 400 KV BISWANATH CHARIALI III (414)AT BALIPARA | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 13/May/2026 | 08:00 | 13/May/2026 | 20:00 |  | R&U works Related Shut Down under PSDF | RQ31776 | Sd deferred
107 | OCC_237 | POWERGRID | 132KV-HAFLONG-JIRIBAM-1 | POWERGRID | D | AMP Works | 13/May/2026 | 09:00 | 13/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31708 | SD may be availed subjected to availability of 132kV Khandong - Umrangsho - Haflong (PG)
110 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 13/May/2026 | 08:00 | 13/May/2026 | 16:00 |  |  | RQ31734 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
17 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-2 L/R@ PALATANA - 400KV | POWERGRID | C | Annual maintenance and testing | 13/May/2026 | 07:00 | 15/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31823 | SD may be availed.
21 | OCC_237 | NEEPCO | 400 KV BNC 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 400 kV BNC-II and Line Reactor-II Panel in Control Room | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31819 | SD may be availed subject to availability of 400KV/132KV RANGANADI-BNC 2. Considering 400KV RANGANADI-BNC 1 as N-1 contigency, Maximum two unit of Ranganadi can only be scheduled during the SD period.When one unit of Ranganadi is scheduled one unit of Pare needs to be scheduled, when two machine of Rangandi is scheduled two machine of Pare is required.
50 | OCC_237 | POWERGRID | 400 KV BISWANATH CHARIALI 4 MAIN BAY (418) AT BALIPARA | POWERGRID | D | AMP OF BAY EQUIPMENT | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31777 | SD may be availed subject to availability of 400kV Balipara – Misa 1 main bay and BNC 3 & Misa 1 tie bay at Balipara
103 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 14/May/2026 | 08:00 | 14/May/2026 | 16:00 |  |  | RQ31723 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required.
104 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 14/May/2026 | 08:00 | 14/May/2026 | 16:00 |  |  | RQ31729 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
172 | OCC_237 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31657 | SD may be availed subject to the availability of 132kV Monarchak - udaipur and 132kV Monarchak - rokhia. Monarchak Generation to kept below 70 MW. SPS at Monarchak may be disabled before avaling shutdown.
237 | OCC_237 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | AEGCL | D | CORRIDOR CLEANING | 14/May/2026 | 10:00 | 14/May/2026 | 16:00 | AGM TSK | R&U works Related Shut Down under PSDF | RQ31621 | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
238 | OCC_237 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 14/May/2026 | 09:30 | 14/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31590 | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
240 | OCC_237 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 | AGM DHALIGAON & AGM RNG | R&U works Related Shut Down under PSDF | RQ31568 | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
241 | OCC_237 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | C | LINE MAINTENANCE & corridor cleaning | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 | AGM PNG | R&U works Related Shut Down under PSDF | RQ31575 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
242 | OCC_237 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 14/May/2026 | 09:00 | 14/May/2026 | 16:00 | AGM GOALPARA T&T & AGM SSJI | R&U works Related Shut Down under PSDF | RQ31604 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
243 | OCC_237 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 135 TO 194 | 14/May/2026 | 08:00 | 14/May/2026 | 16:00 | AGM MNI & AGM NGN T&T | R&U works Related Shut Down under PSDF | RQ31619 | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. RELIABILITY OF THE SYSTEM IS REDUCED.
278 | OCC_237 | MEPTCL | 220KV/132KV MAWNGAP-ICT-2 | MEGHALAYA | D | Checking the NIFPS Fire Detector (FD) trip | 14/May/2026 | 10:00 | 14/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31551 | SD may be availed subject to the availability of 220/132kV Mawngap ICT 1, killing-EPIP-Umtru-Umiam III-Umiam I link and Khleiriat-Mustem-Nehu-Umaim-Umaim 1 link.
279 | OCC_237 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance Work | 14/May/2026 | 08:00 | 14/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31549 | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
12 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-2 | NETC | D | Annual maintenance and testing | 14/May/2026 | 07:00 | 14/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31828 | SD may be availed subject to the availability of 400kV Palatana-Silchar 1, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
51 | OCC_237 | POWERGRID | TIE BAY (423) OF 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV | POWERGRID | D | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 14/May/2026 | 09:00 | 14/May/2026 | 17:00 |  |  | RQ31788 | SD may be availed subject to availability of main bays of 400KV-BGTPP-BONGAIGAON-1 AND 400KV-BONGAIGAON-BYRNIHAT (KILLING) @BONGAIGAON - 400KV
105 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 14/May/2026 | 08:00 | 14/May/2026 | 16:00 |  |  | RQ31735 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
263 | OCC_237 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31600 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service.
26 | OCC_237 | NEEPCO | 132 KV ZIRO BAY AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 132 kV Side Ziro Panel in Control Room | 15/May/2026 | 9:00 | 15/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31814 | SD may be availed subject to availability of 132kV Roing - Pasighat - ALong-Basar - Daporijo link.
280 | OCC_237 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance Work | 15/May/2026 | 08:00 | 15/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31550 | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing.
11 | OCC_237 | OTPCL | 400KV-PALATANA-SILCHAR-2 | NETC | D | Annual maintenance and testing | 15/May/2026 | 07:00 | 15/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31829 | SD may be availed subject to the availability of 400kV Palatana-Silchar 1, 400kV Palatana-SM Nagar-PK Bari-Silchar link. Intimation to NERTS and OTPC
100 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 15/May/2026 | 08:00 | 15/May/2026 | 16:00 |  |  | RQ31730 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
40 | OCC_237 | POWERGRID | ZIRO - 132KV - BUS 1 | POWERGRID | D | FOR AMP WORKS | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31793 | SD may be availed subject to availability of 132kV Roing - Pasighat - ALong-Basar - Daporijo link.
145 | OCC_237 | NEEPCO | HRSG - 2 OF AGTCCPP (STG UNIT 5) - UNIT 5 | NEEPCO | C | Hydrotest of HRSG # 2. | 15/May/2026 | 00:00 | 21/May/2026 | 23:59 | Statutory Compliance | Existing System Normal Maintenance Related Shut Down | RQ31685 | SD may be availed.
171 | OCC_237 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31658 | SD may be availed subject to the availabitiy of 132kV SM Nagar(ISTS) - Budhjungnagar,132kV Agartala - Budhjungnagar, 132kV SM Nagar(ISTS) - SM Nagar and 132kV PK Bari(ISTS) - PK bari
204 | OCC_237 | AEGCL | 220KV/132KV RANGIA -ICT-1 | AEGCL | D | ROUTINE TESTING | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31625 | SD may be availed subject to availability of 220kV/132kV Rangia ICT - 2
234 | OCC_237 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 15/May/2026 | 09:00 | 15/May/2026 | 00:00 | RE BKJ | R&U works Related Shut Down under PSDF | RQ31561 | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
236 | OCC_237 | AEGCL | 400KV-AZARA-SILCHAR | NETC | D | ROUTINE BAY MAITENANCE | 15/May/2026 | 07:00 | 15/May/2026 | 16:00 | AGM MIRZA | R&U works Related Shut Down under PSDF | RQ31622 | S/D may be availed subject to the availability of 400kV Bongaigaon-Azara, 220kV Agia BTPS D/C, Salakati-BTPS D/C and 400kV Bongaiagon-Killing-Silchar link
49 | OCC_237 | POWERGRID | TIE BAY () OF 400KV/132KV SILCHAR-ICT-3 AND FUTURE @SILCHAR - 400KV | POWERGRID | D | AMP Works | 15/May/2026 | 10:00 | 15/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31778 | SD may be availed subject to availability of main bay of ICT-3 and 400/132kV ICT-1 &2 at Silchar.
97 | OCC_237 | POWERGRID | 132KV-RANGANADI-ZIRO-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31709 | SD may be availed subject to availability of 132kV Ziro – Daparijo – Basar – Along – Pasighat – Roing. Bus Reactors at Napir, Roing , Tezu to be in closed condition before availing shutdown. SPS related to outage of 132 kV Panyor LHPS- Ziro (PG) Line to be disabled before availing shutdown.
101 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 15/May/2026 | 08:00 | 15/May/2026 | 16:00 |  |  | RQ31736 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
233 | OCC_237 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | AEGCL | D | CORRIDOR CLEANING | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31554 | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
162 | OCC_237 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Pre-Monsoon Maintenance Work | 15/May/2026 | 09:00 | 15/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31667 | S/D may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW during the shutdown period.
98 | OCC_237 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | POWERGRID | C | Shifting of vulnerable Loc.85, 130 & 133 to the new Tower at respective locations due to M/s NHIDCL road widening project in the same orentation of the line | 15/May/2026 | 08:00 | 29/May/2026 | 16:00 |  | Contruction | RQ31710 | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period. Consent from NEEPCO required
10 | OCC_237 | OTPCL | 400KV/132KV PALATANA-ICT-1 | OTPC | C | Annual maintenance and testing | 16/May/2026 | 07:00 | 2026-05-18 | 16:00 | Annual maintenance and testing |  | RQ31830 | SD may be availed subject to availability of ICT-2. SPS realted to Outage/tripping of both 400/132 kV, 2x125 MVA ICTs at Palatana to be kept ON during the shutdown period if combined demand of Tripura including Bangladesh is more than 460 MW. Dia to be closed at Palatana after availing shutdown.
239 | OCC_237 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | AEGCL | D | CORRIDOR CLEANING | 16/May/2026 | 09:00 | 16/May/2026 | 16:00 | RE GLG | R&U works Related Shut Down under PSDF | RQ31562 | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
235 | OCC_237 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 307 TO 247 | 16/May/2026 | 08:30 | 16/May/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31606 | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
93 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/May/2026 | 08:00 | 16/May/2026 | 16:00 |  |  | RQ31725 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required.
94 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/May/2026 | 08:00 | 16/May/2026 | 16:00 |  |  | RQ31731 | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
96 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 16/May/2026 | 08:00 | 16/May/2026 | 16:30 |  |  | RQ31747 | Sd deferred
170 | OCC_237 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 16/May/2026 | 09:00 | 16/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31659 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar, 132kV Palatana - SM Nagar, 132kV PK Bari - Manu and 132kV PK Bari(ISTS) - PK Bari. SD may be availed after charging of 132kV PK Bari-Manu line.
283 | OCC_237 | MEPTCL | NANGALBIBRA - 132KV - BUS 1 | MEPTCL | D | General maintenance | 16/May/2026 | 08:00 | 16/May/2026 | 12:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31546 | SD may be availed subject to availability 132kV AGia – Mendipathar, 132kV Mawngap – Nongstoin, 132kV Agia – Hastingmari – Ampati – Rongkhon – Ganol link. Consent from Assam is required.
48 | OCC_237 | POWERGRID | BUS COUPLER BAY () OF BALIPARA - 220KV - BUS 1 AND BALIPARA - 220KV - BUS 2 @BALIPARA - 220KV | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 16/May/2026 | 08:00 | 16/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31779 | Sd deferred
95 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 16/May/2026 | 08:00 | 16/May/2026 | 16:00 |  |  | RQ31737 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
221 | OCC_237 | AEGCL | 220KV-TINSUKIA-NTPS-1 | ASSAM | D | CORRIDOR CLEANING | 16/May/2026 | 10:00 | 16/May/2026 | 16:00 | AGM TSK | R&U works Related Shut Down under PSDF | RQ31563 | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
148 | OCC_237 | TSECL | DHARMANAGAR (MISSION TILLA) - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31681 | Sd may be availed subject to the availability of 132kV Hailakandi-Dullavcherra link. Intimation to Assam is required.
181 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31647 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
182 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31648 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
99 | OCC_237 | POWERGRID | 132KV-TEZU-NAMSAI-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/May/2026 | 08:00 | 17/May/2026 | 16:00 |  |  | RQ31724 | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP and Assam is required. FTC procedure to be followed
146 | OCC_237 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31683 | SD may be availed subject to the availability of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
168 | OCC_237 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31660 | SD may be availed subject to the availability of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
169 | OCC_237 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 17/May/2026 | 09:00 | 17/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31661 | SD may be availed subject to the availability of 132kV palatana-Smnagar(TSECL) link, Monarchak-rokhia link needs to be present, SPS at Monarchak needs to be turned OF, Generation of Monarchak needs to be under 70 MW.
92 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 17/May/2026 | 08:00 | 17/May/2026 | 16:00 |  |  | RQ31738 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
47 | OCC_237 | POWERGRID | BUS COUPLER BAY () OF BALIPARA - 220KV - BUS 1 AND BALIPARA - 220KV - BUS 2 @BALIPARA - 220KV | POWERGRID | D | SHUTDOWN OF TIE BAY FOR SPR-4 SLAB CASTING UNDER ADD CAP CONSTRUCTION BY M/S SIEMENS | 18/May/2026 | 08:00 | 18/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31781 | Sd deferred
166 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Pre-Monsoon Maintenance Work | 18/May/2026 | 09:00 | 18/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31663 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
167 | OCC_237 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | TSECL | D | Pre-Monsoon Maintenance Work | 18/May/2026 | 09:00 | 18/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31662 | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
231 | OCC_237 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING LOC 107 TO 111 | 18/May/2026 | 10:00 | 18/May/2026 | 16:00 | RE LEDO | R&U works Related Shut Down under PSDF | RQ31555 | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link.
91 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 18/May/2026 | 08:00 | 18/May/2026 | 16:00 |  |  | RQ31739 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
46 | OCC_237 | POWERGRID | 400 KV BYRNIHAT BAY AT BONGAIGAON | POWERGRID | C | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 18/May/2026 | 09:00 | 21/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31780 | SD may be availed subject to availability of 400kV Bongaigaon - BGTPP I and 400kV Bongaigaon - Byrnihat tie bay and 400kV Bongaigaon - BGTPP I main bay at 400kV Bongaigaon S/S
232 | OCC_237 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 01 TO 108 | 19/May/2026 | 09:30 | 19/May/2026 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | RQ31591 | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link
89 | OCC_237 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 19/May/2026 | 09:00 | 19/May/2026 | 16:00 |  |  | RQ31748 | Sd may be availed subject to the availability of 400kV Biswanath Chariali - Balipara 1,2 and 4
164 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 19/May/2026 | 09:00 | 19/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31665 | Sd may be availed subject to the availability of 132kV SM Nagar(ISTS)-Budhjungnagar and 132kV Surajmaninagar(TSECL)-Budhjungnagar
165 | OCC_237 | TSECL | 132KV-AMBASA-MANU-1 | TSECL | D | Pre-Monsoon Maintenance Work | 19/May/2026 | 09:00 | 19/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31664 | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
226 | OCC_237 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 19/May/2026 | 09:00 | 19/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31599 | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s and 400kV Azara - Silchar should be kept in service.
227 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 75 | 19/May/2026 | 09:00 | 19/May/2026 | 16:00 | AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31613 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
228 | OCC_237 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 19/May/2026 | 08:00 | 19/May/2026 | 16:00 | AGM MNI | R&U works Related Shut Down under PSDF | RQ31557 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
229 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE IN LOC 150-198 | 19/May/2026 | 08:00 | 19/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31582 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
230 | OCC_237 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | AEGCL | D | ROUTINE BAY MAITENANCE | 19/May/2026 | 07:00 | 19/May/2026 | 16:00 | AGM MIRZA AGM SSJI | R&U works Related Shut Down under PSDF | RQ31608 | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link.
90 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 19/May/2026 | 08:00 | 19/May/2026 | 16:00 |  |  | RQ31740 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
3 | OCC_237 | OTPCL | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | ENICL | D | Annual maintenance and testing | 20/May/2026 | 07:00 | 20/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31837 | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On condtion during shutdown period.
87 | OCC_237 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 20/May/2026 | 09:00 | 20/May/2026 | 16:00 |  |  | RQ31749 | Sd may be availed subject to the availability of 400kV Biswanath Chariali - Balipara 1,2 and 4
88 | OCC_237 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | POWERGRID | D | Installation of TLSA ( TRANSMISSION LINE SURGE ARRESTER) | 20/May/2026 | 08:00 | 20/May/2026 | 16:00 |  |  | RQ31741 | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link.
163 | OCC_237 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 20/May/2026 | 09:00 | 20/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31666 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown.
222 | OCC_237 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 20/May/2026 | 09:00 | 20/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31601 | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s , 400kV Silchar - Azara should be kept in service.
223 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 76 TO 155 | 20/May/2026 | 09:00 | 20/May/2026 | 16:00 | AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31614 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
224 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-2 | POWERGRID | D | LINE MAINTENANCE IN LOC 35-68 | 20/May/2026 | 08:00 | 20/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31585 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
225 | OCC_237 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | AEGCL | D | ROUTINE BAY MAITENANCE | 20/May/2026 | 07:00 | 20/May/2026 | 16:00 | AGM MIRZA | R&U works Related Shut Down under PSDF | RQ31609 | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link.
286 | OCC_237 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 121 to 119. | 20/May/2026 | 10:00 | 20/May/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31543 | SD may be availed
86 | OCC_237 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | NAGALAND,DOP | C | CB Mechanism replacment works | 20/May/2026 | 09:00 | 21/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31711 | SD may be availed subject to availability of 132kV Imphal- Gamphazol-Karong-Kohima and 132kV Doyang-Sanis-Wokhoa-Chiephbozou-Kohima link
277 | OCC_237 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | MEGHALAYA | D | Maintenance Work | 20/May/2026 | 08:00 | 20/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31553 | SD may be availed subject to availability of 220kV Mawngap - Killing 1, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
134 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 21/May/2026 | 08:00 | 21/May/2026 | 16:30 |  |  | RQ31714 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
160 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Pre-Monsoon Maintenance Work | 21/May/2026 | 09:00 | 21/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31669 | S/D may be availed 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
161 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 21/May/2026 | 09:00 | 21/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31668 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.
217 | OCC_237 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | MSPCL,AEGCL | D | PREVENTIVE MAINTENANCE | 21/May/2026 | 09:00 | 21/May/2026 | 16:00 | RE PLP | R&U works Related Shut Down under PSDF | RQ31597 | S/D may be availed subject to 132kV Srikona-Pailapool, 132kV Badarpur-Jiribam(PG) and 132kV Haflong(PG)-Jiribam(PG) link.
218 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 75 | 21/May/2026 | 09:00 | 21/May/2026 | 16:00 | AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31615 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
219 | OCC_237 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 21/May/2026 | 08:00 | 21/May/2026 | 16:00 | AGM MNI | R&U works Related Shut Down under PSDF | RQ31558 | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
220 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 237 TO 162 | 21/May/2026 | 08:00 | 21/May/2026 | 15:00 | AGM SMG | R&U works Related Shut Down under PSDF | RQ31579 | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
276 | OCC_237 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | MEGHALAYA | D | Maintenance Work | 21/May/2026 | 08:00 | 21/May/2026 | 16:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31552 | SD may be availed subject to availability of 220kV Mawngap - Killing 2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present.
2 | OCC_237 | OTPCL | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | ENICL | D | Annual maintenance and testing | 21/May/2026 | 07:00 | 21/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31838 | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
85 | OCC_237 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 21/May/2026 | 09:00 | 21/May/2026 | 16:00 |  |  | RQ31750 | Sd may be availed
131 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 22/May/2026 | 08:00 | 22/May/2026 | 16:30 |  |  | RQ31715 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
1 | OCC_237 | OTPCL | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | ENICL | D | Annual maintenance and testing | 22/May/2026 | 07:00 | 22/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31839 | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
159 | OCC_237 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | TRIPURA | D | Pre-Monsoon Maintenance Work | 22/May/2026 | 09:00 | 22/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31670 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) - SM Nagar, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. SD may be availed after charging of 132kV PK Bari-Manu line.
214 | OCC_237 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 76 TO 155 | 22/May/2026 | 09:00 | 22/May/2026 | 16:00 | AGM NAGAON T&T | R&U works Related Shut Down under PSDF | RQ31616 | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
215 | OCC_237 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 307 TO 247 | 22/May/2026 | 08:30 | 22/May/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31607 | S/D may be availed. 220 kV Agia - Boko line, 220 kV Agia - Mirza line and 400kV Bongaigaon - Mirza, ICTs at Mirza to be kept in service
216 | OCC_237 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE AT LOC 7 TO 53 | 22/May/2026 | 08:00 | 22/May/2026 | 15:00 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31612 | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
83 | OCC_237 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-4 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 22/May/2026 | 09:00 | 22/May/2026 | 16:00 |  |  | RQ31751 | Sd may be availed subject to availability of 400kV BNC - Balipra 1,2 and 3
129 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 23/May/2026 | 08:00 | 23/May/2026 | 16:30 |  |  | RQ31716 | Sd may be availed subject to the availability of 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link.
173 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 23/May/2026 | 09:00 | 23/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31656 | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia and 132kV Monarchak-Udaipur-Palatana needs to be present. Combined loading of 132kV Monarchak-Udaipur and 132kV Agartal-Rokhia 2 needs to be under 70MW.
9 | OCC_237 | OTPCL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Annual maintenance and testing | 23/May/2026 | 07:00 | 23/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31833 | SD may be availed subject to the availability of 132kV Monarchak - udaipur and 132kV Monarchak - rokhia. Monarchak Generation to kept below 70 MW. SPS at Monarchak may be disabled before avaling shutdown.
153 | OCC_237 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 23/May/2026 | 09:00 | 23/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31676 | SD may be availed subject to the availability of 132kV Monarchak - udaipur and 132kV Monarchak - rokhia. Monarchak Generation to kept below 70 MW. SPS at Monarchak may be disabled before avaling shutdown.
126 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 24/May/2026 | 08:00 | 24/May/2026 | 16:30 |  |  | RQ31717 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
147 | OCC_237 | TSECL | AMBASA - 132KV - BUS 1 | TSECL | D | Pre-Monsoon Maintenance Work | 24/May/2026 | 09:00 | 24/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31682 | SD may be availed subject to availability of 132kV Budjungnagar – Jirinia – Gamaitila. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa Bus 132kV Manu S/S will be black out.
178 | OCC_237 | TSECL | 132KV-AMBASA-MANU-1 | TSECL | D | Pre-Monsoon Maintenance Work | 24/May/2026 | 09:00 | 24/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31649 | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
180 | OCC_237 | TSECL | 132KV-AMBASA-GAMATILLA-1 | TSECL | D | Pre-Monsoon Maintenance Work | 24/May/2026 | 09:00 | 24/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31651 | SD may be availed subject to availability of 132kV Budjungnagar – Jirinia – Gamaitila and 132kV PK abri (ISTS) – Manu – Ambasa
144 | OCC_237 | NEEPCO | HRSG - 1 OF AGTCCPP (STG UNIT 5) - UNIT 5 | NEEPCO | C | Hydrotest of HRSG #1 | 24/May/2026 | 00:00 | 30/May/2026 | 23:59 | Statutory compliance | Existing System Normal Maintenance Related Shut Down | RQ31686 | SD may be availed.
122 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 25/May/2026 | 08:00 | 25/May/2026 | 16:30 |  |  | RQ31718 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
7 | OCC_237 | OTPCL | 132KV-PALATANA-SURAJMANI NAGAR-1 | POWERGRID | D | Annual maintenance and testing | 25/May/2026 | 07:00 | 25/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31831 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown.
81 | OCC_237 | POWERGRID | 132KV-BADARPUR-KHLIEHRIAT-1 | POWERGRID | D | Installation of insulation sleeve at loc no 49-50 by Silchar TLM | 25/May/2026 | 08:00 | 25/May/2026 | 16:00 |  | R&U works Related Shut Down under PSDF | RQ31713 | SD may be availed subject to availability of 132kV Badarpur – Panchgram – Lunshnong-Khliehriat link, 132kV Khandong – Khleihriat link, 220kV Killing – Mawngap D/C
82 | OCC_237 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 25/May/2026 | 08:00 | 25/May/2026 | 16:00 |  |  | RQ31752 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
157 | OCC_237 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | TSECL | D | Pre-Monsoon Maintenance Work | 25/May/2026 | 09:00 | 25/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31672 | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
158 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Pre-Monsoon Maintenance Work | 25/May/2026 | 09:00 | 25/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31671 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
213 | OCC_237 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING AT LOC 42 TO 74 | 25/May/2026 | 08:30 | 25/May/2026 | 16:30 | AGM SSJI | R&U works Related Shut Down under PSDF | RQ31577 | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
45 | OCC_237 | POWERGRID | BTPS(NTPC) II (FUTURE) & 2X 80 MVAR BUS REACTOR III AND IVAT BONGAIGAON | POWERGRID | C | CB MECHANISM OVERHAULING WORKS AT 400KV BONGAIGAON S/S. | 25/May/2026 | 09:00 | 28/May/2026 | 17:00 |  | R&U works Related Shut Down under PSDF | RQ31782 | SD may be availed subject to the availability of NTPC- Bongaigaon ckt 1 and Ckt 2 must be charged though main bay
121 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 26/May/2026 | 08:00 | 26/May/2026 | 16:30 |  |  | RQ31719 | SD may availed subject to availability of 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
24 | OCC_237 | NEEPCO | 132 KV PARE BAY AT RANGANADI | NEEPCO | D | Installation of new ABT Management System on 132 kV Side Pare Panel in Control Room | 11/May/2026 | 09:00 | 11/May/2026 | 16:00 | Shutdown may be availed for necessary isolation during installation work | Existing System Improvement Related Shut Down | RQ31816 | SD may be availed subject to availability of 132kV Panyor – Itanagar, 132kV Panyor – Lekhi, 400/132kV ICT 1&2 at Panyor.
6 | OCC_237 | OTPCL | 132KV-PALATANA-SURAJMANI NAGAR-1 | POWERGRID | D | Annual maintenance and testing | 26/May/2026 | 07:00 | 26/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31832 | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown.
80 | OCC_237 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 26/May/2026 | 08:00 | 26/May/2026 | 16:00 |  |  | RQ31753 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
119 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 27/May/2026 | 08:00 | 27/May/2026 | 16:30 |  |  | RQ31742 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
79 | OCC_237 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 27/May/2026 | 08:00 | 27/May/2026 | 16:00 |  |  | RQ31754 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
5 | OCC_237 | OTPCL | 132KV/6.6KV PALATANA-ICT-1 | OTPC | C | Annual maintenance and testing | 27/May/2026 | 07:00 | 29/May/2026 | 16:00 | Annual maintenance and testing |  | RQ31835 | SD may be availed subject to availability of 132/6.6kV SST-2 at Palatana
115 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 28/May/2026 | 08:00 | 28/May/2026 | 16:30 |  |  | RQ31743 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
78 | OCC_237 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 28/May/2026 | 08:00 | 28/May/2026 | 16:00 |  |  | RQ31755 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
156 | OCC_237 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Pre-Monsoon Maintenance Work | 28/May/2026 | 09:00 | 28/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31673 | S/D may be availed subject to availability of 132kV Palatana-Udaipur, 132kV Monarchak-Rokhia and 132kV Rokhia-Agartala D/C. Monarchak Generation may be kept to 70 MW. SPS at Monarchak to be kept off before availing shutdown. before final charging of the line
212 | OCC_237 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 28/May/2026 | 09:00 | 28/May/2026 | 16:00 | AGM GOALPARA T&T | R&U works Related Shut Down under PSDF | RQ31603 | S/D may be availed. 220 kV Mirza - Boko line, 220 kV Agia - Mirza & 400kV Bongaigaon - Mirza and ICTs to be kept in service.
285 | OCC_237 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 118 to 116 | 28/May/2026 | 10:00 | 28/May/2026 | 15:00 | Avail | Existing System Normal Maintenance Related Shut Down | RQ31544 | SD may be availed
111 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 29/May/2026 | 08:00 | 29/May/2026 | 16:30 |  |  | RQ31744 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
154 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | AEGCL,TSECL | D | Pre-Monsoon Maintenance Work | 29/May/2026 | 09:00 | 29/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31675 | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link, Intimation to Assam
155 | OCC_237 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | TRIPURA | D | Pre-Monsoon Maintenance Work | 29/May/2026 | 09:00 | 29/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31674 | SD may be availed subject to the availability of 132kV Sm Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. SD may be availed after charging of 132kV PK Bari-Manu line.
209 | OCC_237 | AEGCL | 220KV-TINSUKIA-NRPP-1 | ASSAM | D | CORRIDOR CLEANING | 29/May/2026 | 10:00 | 29/May/2026 | 16:00 | AGM TSK | R&U works Related Shut Down under PSDF | RQ31564 | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
210 | OCC_237 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 29/May/2026 | 08:30 | 29/May/2026 | 16:30 | AGM GOALPARA T&T & AGM SSJI | R&U works Related Shut Down under PSDF | RQ31605 | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
211 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-1 | POWERGRID | D | LINE MAINTENANCE IN LOC 199-249 | 29/May/2026 | 08:00 | 29/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31583 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
77 | OCC_237 | POWERGRID | 132KV-PASIGHAT-ROING-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 29/May/2026 | 08:00 | 29/May/2026 | 16:00 |  |  | RQ31756 | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
4 | OCC_237 | OTPCL | 132KV/6.6KV PALATANA-ICT-2 | OTPC | C | Annual maintenance and testing | 30/May/2026 | 07:00 | 01/Jun/2026 | 16:00 | Annual maintenance and testing |  | RQ31836 | SD may be availed subject to availability of 132/6.6kV SST-1 at Palatana
106 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 30/May/2026 | 08:00 | 30/May/2026 | 16:30 |  |  | RQ31745 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
207 | OCC_237 | AEGCL | 132KV-TINSUKIA-LEDO-1 | AEGCL | D | CORRIDOR CLEANING AT LOC 01 TO 108 | 30/May/2026 | 09:30 | 30/May/2026 | 16:00 | RE RUPAI | R&U works Related Shut Down under PSDF | RQ31593 | SD may be availed subject to the availability of 132kV Tinsukia-Rupai -LEDO link.
208 | OCC_237 | AEGCL | 132KV-GOHPUR-NALKATA-2 | POWERGRID | D | LINE MAINTENANCE IN LOC 69-100 | 30/May/2026 | 08:00 | 30/May/2026 | 15:00 | AGM NORTH LAKHIMPUR | R&U works Related Shut Down under PSDF | RQ31586 | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
102 | OCC_237 | POWERGRID | 132KV-AIZWAL-KUMARGHAT-1 | POWERGRID | D | Balance TLA installation work in 132KV Aizawl-Kumarghat TL in hilly terrains areas by head weight. | 31/May/2026 | 08:00 | 31/May/2026 | 16:30 |  |  | RQ31746 | 132kV Badarpur-Kolasib-Aizawl link, silchar-melriat-Aizawl link and Aizawl-Tipaimukh-Jiribam link needs to be present.
151 | OCC_237 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Pre-Monsoon Maintenance Work | 31/May/2026 | 09:00 | 31/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31678 | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
152 | OCC_237 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Pre-Monsoon Maintenance Work | 31/May/2026 | 09:00 | 31/May/2026 | 16:00 |  | Existing System Normal Maintenance Related Shut Down | RQ31677 | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link.