## Sheet1
SL No. | occ number | name of requesting agency | element name | owner | daily/ continous | reason | shutdown start date | shutdown start time | shutdown end date | shutdown end time | requester remarks | outage status | request type | tag | reference number | unnamed: 27 | Study remarks | Proposed
1 | OCC_238 | POWERGRID | 400KV/132KV BISWANATH CHARIALI-ICT-2 | POWERGRID | D | AMP works | 01/Jun/2026 | 8:00 | 01/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32168 |  | Sd may be availed subject to the availability of 400/132kV ICT1 at BNC, 132kV Ranganadi-Lekhi, 132kV Ranaganadi-Pare, 132kV Ranganadi-Chimpu-BNC link, 400/132kV ICT 1 and 2 at Panyor. Under N-1 condition of 400KV/132KV BISWANATH CHARIALI-ICT-2, Atleast one machine of pare and one machine of Ranganadi needs to be scheduled duirng the SD period
2 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 01/Jun/2026 | 8:00 | 01/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32156 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
3 | OCC_238 | POWERGRID | 132KV-DIMAPUR-DIMAPUR(PG)-1 | NAGALAND,POWERGRID,DOP | D | Warranty Testing on GIS Bays at Dimapur SS | 01/Jun/2026 | 10:00 | 01/Jun/2026 | 15:00 |  | Requested | PLANNED |  | RQ32154 |  | Sd may be availed subject to availability of 132kV Dimapur(PG) - Dimapur ckt-2, SPS related to tripping of either ckt of 132kV Dimapur(PG) - Dimapur to be kept in off conditon before availing shutdown. Loading of 132kV Dimapur(PG) - Dimapur ckt-2 to be maintained below 80 MW. Nagaland consent is required. | 10:00 to 15:00
4 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 01/Jun/2026 | 07:00 | 01/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32021 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
5 | OCC_238 | POWERGRID | 220 KV, 50 MVA ICT 2 BAY AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Note - ICT-2 shall remain charged though TBC bay | 02/Jun/2026 | 14:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32175 |  | SD may be availed subject to no outage of element | 14:00-16:00
6 | OCC_238 | POWERGRID | 220 KV, 50 MVA ICT 1 BAY AT SALAKATI | POWERGRID | D | SF6 quality testing of CB. Note - ICT-1 shall remain charged though TBC bay | 02/Jun/2026 | 9:00 | 02/Jun/2026 | 12:00 |  | Requested | PLANNED |  | RQ32174 |  | SD may be availed subject to no outage of element | 09:00 -12:00
7 | OCC_238 | POWERGRID | 220 KV MISA 1 BAY AT SAMAGURI | POWERGRID | C | CB Mechanism overhauling works. It may be noted that Line was charged through Bus coupler. | 20/Jun/2026 | 8:00 | 22/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32173 |  | Sd may be availed subject to no outage of elements | 20/Jun/2026 to 22/Jun/2026
8 | OCC_238 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 27/Jun/2026 | 09:00 | 27/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32085 |  | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. | 27/Jun/2026
9 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 02/Jun/2026 | 8:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32157 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, 220kV BTPS-Agia D/C. Consent from Assam
10 | OCC_238 | POWERGRID | 400KV-MISA-MARIANI (PG)-2 | POWERGRID | D | Replacement of flashover disc insulators (5 nos), Y Phase of Loc 440 at 400 kV Mariani Misa TL CKT II by Mariani TLM | 02/Jun/2026 | 08:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32134 |  | SD may be availed subject to the availability of 400kV Misa-Mariani (PG) 1, 400kV New Kohima-Mariani(PG) link
11 | OCC_238 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Kumarghat TLM | 02/Jun/2026 | 08:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32135 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 2, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link.
12 | OCC_238 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | POWERGRID | D | AMP of Bay and line equipments at Badarpur SS | 02/Jun/2026 | 08:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32137 |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2.
13 | OCC_238 | POWERGRID | 132KV-AIZWAL-KOLASIB-1 | POWERGRID | D | Warranty Testing on Kolasib Bay at Aizawl S/S | 02/Jun/2026 | 08:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32138 |  | Shutdown may be availed subject to availability of 132kV Badarpur - Kolasib,132kV Aizwal - Melriat,132kV Melriat - Zungtai, 132kV Aizwal - Kumarghat and 132kV Jiribam - Tipaimukh. SD may be allowed after returning of 132kV Melriat(PG) - Zuagtai line
14 | OCC_238 | POWERGRID | 132KV-DIMAPUR-DIMAPUR(PG)-1 | NAGALAND,POWERGRID,DOP | D | Warranty Testing on GIS Bays at Dimapur SS | 02/Jun/2026 | 10:00 | 02/Jun/2026 | 15:00 |  | Requested | PLANNED |  | RQ32155 |  | Sd may be availed subject to availability of 132kV Dimapur(PG) - Dimapur ckt-2, SPS related to tripping of either ckt of 132kV Dimapur(PG) - Dimapur to be kept in off conditon before availing shutdown. Loading of 132kV Dimapur(PG) - Dimapur ckt-2 to be maintained below 80 MW. Nagaland consent is required.
15 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 02/Jun/2026 | 07:00 | 02/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32022 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
16 | OCC_238 | POWERGRID | MAIN BAY () OF 220KV-BONGAIGAON-SALAKATI-2 @SALAKATI - 220KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 03/Jun/2026 | 14:00 | 03/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32178 |  | Sd may be availed. | 14:00-16:00
17 | OCC_238 | POWERGRID | 220KV MAIN BAY OF 220KV/132KV SALAKATI-ICT-3 @SALAKATI - 220KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 03/Jun/2026 | 9:00 | 03/Jun/2026 | 12:00 |  | Requested | PLANNED |  | RQ32176 |  | SD may be availed subject to no outage of elements. | 09:00 -12:00
18 | OCC_238 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | AEGCL | D | CORRIDOR CLEANING LOC 38-82 | 03/Jun/2026 | 10:00 | 03/Jun/2026 | 16:00 | AGM TINSUKIA | Requested | PLANNED |  | RQ32107 |  | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
19 | OCC_238 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | Tightening of nuts and bolts between Tower Location 111 to 109. | 03/Jun/2026 | 10:00 | 03/Jun/2026 | 15:00 | Avail | Requested | PLANNED |  | RQ32208 |  | SD may be availed subject to availability of 220kV New Shillong-Mawngap 2 line
20 | OCC_238 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Jun/2026 | 09:30 | 03/Jun/2026 | 16:00 | AGM PANCHGRAM | Requested | PLANNED |  | RQ32082 |  | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
21 | OCC_238 | PENTL | 220KV-AGBPP GIS-NAMSAI GIS-2 | PENTL | D | Attending of shutdown nature defects | 23/Jun/2026 | 09:00 | 23/Jun/2026 | 15:30 |  | Requested | PLANNED |  | RQ32132 |  | Sd may availed subject to availibility of 220kV AGBPP - Namsai ckt-1, 132kV Panyor-Ziro-Daparijo-Along-Basar-Pasighat-Roing-Tesu-Namsai link. 50 MVAR BR at 220kV Namsai S/S need to be kept in off condtion during the shutdown period. Intimation to AP | 23/Jun/2026
22 | OCC_238 | POWERGRID | TIE BAY () OF 400KV-PALATANA-SILCHAR-1 AND SILCHAR - 400KV B/R 2 @SILCHAR - 400KV | POWERGRID | D | AMP works | 03/Jun/2026 | 09:00 | 03/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32177 |  | SD may be availed subject to availability of 400kV Palatan - Silchar I main bay and 400kV BR2 main bay at 400kV Silchar S/S
23 | OCC_238 | AEGCL | 132KV-AGIA-MENDIPATHER-1 | MEPTCL | D | ROUTINE TESTING | 03/Jun/2026 | 09:00 | 03/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32106 |  | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Consent from Meghalaya
24 | OCC_238 | POWERGRID | 132KV-BISWANATH CHARIALI-GOHPUR-1 | INDIGRID | D | AMP OF BAY EQUIPMENTS | 03/Jun/2026 | 09:00 | 03/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32139 |  | Sd may be availed. Consent from Assam
25 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 03/Jun/2026 | 8:00 | 03/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32158 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
26 | OCC_238 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 42 TO 74 | 03/Jun/2026 | 08:30 | 03/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32079 |  | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
27 | OCC_238 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Jun/2026 | 08:00 | 03/Jun/2026 | 16:00 | AGM MNI | Requested | PLANNED |  | RQ32067 |  | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
28 | OCC_238 | POWERGRID | 400KV-NEW KOHIMA-MARIANI (PG)-2 | KMTL | D | Relay testing works | 03/Jun/2026 | 08:00 | 03/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32136 |  | SD may be availed subject to the availability of 400kV New Kohima - Mariani 1 and 400kV Silchar - Imphal D/C. Intimation to KMTL
29 | OCC_238 | POWERGRID | 132KV-DIMAPUR-DIMAPUR(PG)-2 | NAGALAND,DOP | D | Warranty Testing on GIS Bays at Dimapur SS | 03/Jun/2026 | 08:00 | 03/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32159 |  | Sd may be availed subject to availability of 132kV Dimapur(PG) - Dimapur ckt-1, SPS related to tripping of either ckt of 132kV Dimapur(PG) - Dimapur to be kept in off conditon before availing shutdown. Loading of 132kV Dimapur(PG) - Dimapur ckt-1 to be maintained below 80 MW. Nagaland consent is required.
30 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 03/Jun/2026 | 07:00 | 03/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32023 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
31 | OCC_238 | POWERGRID | 220 KV ALIPURDUAR 2 BAY (204) AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 04/Jun/2026 | 14:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32181 |  | Sd may be availed subject to no outage of elements. Intimation to NLDC | 14:00-16:00
32 | OCC_238 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | MSPCL | D | Monthly change of 3*105MVA transfer (R,Y&B phase will be charged) | 10/Jun/2026 | 11:30 | 10/Jun/2026 | 13:30 | No load will be affected | Requested | PLANNED |  | RQ32009 |  | SD may be availed subject to availability of 132kV Imphal – Yingagangpokpi-Kongba-New Thoubal – Old Thoubal – Kakching – Churachandpur – Ningthoukhong link. Manipur demand to be kept below 170 MW to avoid low voltage under n-1 contingecy of 132kV Ningthoukhong – Churachandpur II. | 10/Jun/2026
33 | OCC_238 | POWERGRID | 220 KV ALIPURDUAR 1 BAY (203) AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 04/Jun/2026 | 9:00 | 04/Jun/2026 | 12:00 |  | Requested | PLANNED |  | RQ32179 |  | Sd may be availed subject to no outage of elements. Intimation to NLDC | 09:00-12:00
34 | OCC_238 | PENTL | 220KV-AGBPP GIS-NAMSAI GIS-2 | PENTL | D | Attending of shutdown nature defects | 22/Jun/2026 | 09:00 | 22/Jun/2026 | 15:30 |  | Requested | PLANNED |  | RQ32133 |  | Sd may availed subject to availibility of 220kV AGBPP - Namsai ckt-1, 132kV Panyor-Ziro-Daparijo-Along-Basar-Pasighat-Roing-Tesu-Namsai link. 50 MVAR BR at 220kV Namsai S/S need to be kept in off condtion duringthe shutdown period.Intimation to AP | 22/Jun/2026
35 | OCC_238 | AEGCL | 132KV-AGIA-NANGALBIBRA-1 | MEPTCL | D | ROUTINE TESTING | 04/Jun/2026 | 09:00 | 04/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32071 |  | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Consent from Meghalaya
36 | OCC_238 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | AEGCL | D | CORRIDOR CLEANING | 04/Jun/2026 | 09:00 | 04/Jun/2026 | 16:00 | RE GLG | Requested | PLANNED |  | RQ32083 |  | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
37 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 04/Jun/2026 | 8:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32161 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
38 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | TSECL | D | Routine Maintenance Work | 04/Jun/2026 | 09:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32027 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
39 | OCC_238 | POWERGRID | 400KV/132KV IMPHAL(PG)-ICT-2 | POWERGRID | D | AMP works | 04/Jun/2026 | 7:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32167 |  | Sd may be availed subject to the availability of 400/132kv ICT1 at Imphal, 132kv Dimapur-Imphal link, 400/132kV ICT at Thoubal. Intimation to Manipur.
40 | OCC_238 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Jun/2026 | 08:00 | 04/Jun/2026 | 16:00 | AGM MNI | Requested | PLANNED |  | RQ32068 |  | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
41 | OCC_238 | POWERGRID | 132KV-DIMAPUR-DIMAPUR(PG)-2 | NAGALAND,DOP | D | Warranty Testing on GIS Bays at Dimapur SS | 04/Jun/2026 | 08:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32160 |  | Sd may be availed subject to availability of 132kV Dimapur(PG) - Dimapur ckt-1, SPS related to tripping of either ckt of 132kV Dimapur(PG) - Dimapur to be kept in off conditon before availing shutdown. Loading of 132kV Dimapur(PG) - Dimapur ckt-1 to be maintained below 80 MW. Nagaland consent is required.
42 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 04/Jun/2026 | 07:00 | 04/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32024 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
43 | OCC_238 | POWERGRID | TRANSFER BUS COUPLER BAY (202) OF (SALAKATI - 220KV - BUS 1 & SALAKATI - 220KV - BUS 2) AND SALAKATI - 220KV - BUS 3 @SALAKATI - 220KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 05/Jun/2026 | 14:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32182 |  | Shutdown may be availed | 14:00 - 16:00
44 | OCC_238 | POWERGRID | BUS COUPLER BAY () OF SALAKATI - 220KV - BUS 1 AND SALAKATI - 220KV - BUS 2 @SALAKATI - 220KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 05/Jun/2026 | 9:00 | 05/Jun/2026 | 12:00 |  | Requested | PLANNED |  | RQ32185 |  | Shutdown may be availed. Proper segregation of elements to be ensured before availing the shutdown. | 09:00 - 12:00
45 | OCC_238 | POWERGRID | MAIN BAY (202) OF 400KV/220KV BALIPARA-ICT-1 @BALIPARA - 220KV | POWERGRID | D | AMP OF BAY EQUIPMENTS AT BALIPARA S/S. Note ICT shall remain charged through TBC Bay. | 05/Jun/2026 | 8:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32183 |  | SD may be availed subject to outage of elements. ICT-1 may be charged through transfer bus.
46 | OCC_238 | POWERGRID | MAIN BAY (1) OF 400KV/132KV BISWANATH CHARIALI-ICT-2 @BISWANATH CHARIALI - 400KV | POWERGRID | D | AMP works | 05/Jun/2026 | 09:00 | 05/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32184 |  | Sd may be availedsubject to the availability of main bay of 400/132 kV 200 MVA ICT 1, tie bay of 400/132 kV 200MVA ICT 2 and 400/132 kV 200 MVA ICT 1 | Dia must be updated
47 | OCC_238 | POWERGRID | MAIN BAY () OF 132KV/33KV KUMARGHAT-ICT-1 @KUMARGHAT - 132KV | POWERGRID | D | Warranty testing for GIS bays | 05/Jun/2026 | 09:00 | 05/Jun/2026 | 18:00 |  | Requested | PLANNED |  | RQ32206 |  | SD may be availed.
48 | OCC_238 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/Jun/2026 | 09:00 | 05/Jun/2026 | 16:00 | AGM PANCHGRAM | Requested | PLANNED |  | RQ32080 |  | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
49 | OCC_238 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32087 |  | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. | 08/Jun/2026
50 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 05/Jun/2026 | 8:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32162 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
51 | OCC_238 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Routine Maintenance Work | 05/Jun/2026 | 09:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32028 |  | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcheera-Dharmanagar link. Intimation to Assam
52 | OCC_238 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 7 TO 52 | 05/Jun/2026 | 08:30 | 05/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32098 |  | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
53 | OCC_238 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Kumarghat TLM | 05/Jun/2026 | 08:00 | 05/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32140 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 1, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link. Intimation to INDIGRID
54 | OCC_238 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | POWERGRID | D | For replacement of flashover insulator during tripping dated 22.04.2026 At Loc 152 and 195 By Dimapur TLM | 05/Jun/2026 | 08:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32141 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-II ckt. Intimation to NEEPCO
55 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 05/Jun/2026 | 07:00 | 05/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32025 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
56 | OCC_238 | POWERGRID | 220 KV BTPS (AEGCL) 2 BAY (207) AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay. 208 Bay is 220 Salakati - BTPS#2 Bay | 06/Jun/2026 | 15:00 | 06/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32187 |  | Sd may be availed subject to no outage of elements.
57 | OCC_238 | POWERGRID | 220 KV BTPS (AEGCL) 1 BAY (208) AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay . 207 Bay is 220 Salakati - BTPS#1 Bay | 06/Jun/2026 | 10:00 | 06/Jun/2026 | 13:00 |  | Requested | PLANNED |  | RQ32186 |  | Sd may be availed subject to no outage of elements.
58 | OCC_238 | POWERGRID | MAIN BAY () OF 132KV/33KV KUMARGHAT-ICT-1 @KUMARGHAT - 132KV | POWERGRID | D | Warranty testing for GIS bays | 06/Jun/2026 | 09:00 | 06/Jun/2026 | 18:00 |  | Requested | PLANNED |  | RQ32207 |  | Sd may be availed
59 | OCC_238 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | AEGCL | D | CORRIDOR CLEANING LOC 76 TO 159 | 06/Jun/2026 | 09:00 | 06/Jun/2026 | 16:00 | RE RUPAI | Requested | PLANNED |  | RQ32064 |  | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
60 | OCC_238 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Jun/2026 | 09:00 | 06/Jun/2026 | 16:00 | AGM PANCHGRAM | Requested | PLANNED |  | RQ32078 |  | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
61 | OCC_238 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | AEGCL,POWERGRID | D | 220 kV Balipara-Sonabil Shutdown is taken against saver clamp installation for strengthening of MSCJ in the line. | 06/Jun/2026 | 8:00 | 06/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32163 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam
62 | OCC_238 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Routine Maintenance Work | 06/Jun/2026 | 09:00 | 06/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32030 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link and 132kV Rabindranagar - Rokhia line.
63 | OCC_238 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 1 TO 25 | 06/Jun/2026 | 08:30 | 06/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32097 |  | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
64 | OCC_238 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | POWERGRID | D | For replacement of flashover insulator during AR dated 25.04.2026 At Loc 166 By Dimapur TLM | 06/Jun/2026 | 08:00 | 06/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32142 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-I. Intimation to NEEPCO
65 | OCC_238 | MEPTCL | MENDIPATHER - 132KV - BUS 1 | MEPTCL | D | Preventive maintenance work | 06/Jun/2026 | 08:00 | 06/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32111 |  | SD may be availed, Subject to availability of 132 kV Nangalbibra-Agia, 132kV Nangalbibra-Nongstoin-Mawngap link, 132kV Nangalbibra-Rongkhon-Ampati-Hastingmari-Agia link. Under N-1 of 132kV Mawngap-Nongstoin availability of Ganol generation is preferable for maintaining better voltage profile at Tura, Ganol, Ampati etc area .Intimation to Assam
66 | OCC_238 | MEPTCL | MENDIPATHER - 132KV - BUS 2 | MEPTCL | D | Preventive maintenance work | 06/Jun/2026 | 08:00 | 06/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32112 |  | SD may be availed, Subject to availability of 132 kV Nangalbibra-Agia, 132kV Nangalbibra-Nongstoin-Mawngap link, 132kV Nangalbibra-Rongkhon-Ampati-Hastingmari-Agia link. Under N-1 of 132kV Mawngap-Nongstoin availability of Ganol generation is preferable for maintaining better voltage profile at Tura, Ganol, Ampati etc area .Intimation to Assam
67 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 1 | DOP,ARUNACHAL PRADESH | D | Modification of switching Arrangment | 06/Jun/2026 | 07:00 | 06/Jun/2026 | 15:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32214 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
68 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 2 | DOP,ARUNACHAL PRADESH | D | Modification of switching Arrangment | 06/Jun/2026 | 07:00 | 06/Jun/2026 | 15:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32215 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
69 | OCC_238 | Arunachal Pradesh | 132KV-LEKHI-RANGANADI-1 | POWERGRID,DOP | C | Removal of line bay jumpering other mandatory work | 06/Jun/2026 | 07:00 | 08/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32219 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 • Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period during the off peak hours. The sequence of Unit synchronisation are as follows: Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the off peak hours of shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
70 | OCC_238 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Routine Maintenance Work | 07/Jun/2026 | 09:00 | 07/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32029 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link and 132kV Rabindranagar - Rokhia line.
71 | OCC_238 | Arunachal Pradesh | 132KV-BALIPARA-TENGA-1 | ARUNACHAL PRADESH | D | Vegetation Clearance | 07/Jun/2026 | 07:00 | 07/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32125 |  | Sd may be availed subject to the availability of 132kV Kameng-Khupi-Tenga link
72 | OCC_238 | POWERGRID | 132 KV, 50 MVA ICT 1 BAY AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 08/Jun/2026 | 15:00 | 08/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32190 |  | SD may be availed subject to the availability of other ICTs
73 | OCC_238 | POWERGRID | MAIN BAY () OF 220KV-BONGAIGAON-SALAKATI-1 @SALAKATI - 220KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 08/Jun/2026 | 10:00 | 08/Jun/2026 | 13:00 |  | Requested | PLANNED |  | RQ32188 |  | Sd may be availed subject to no outage of elements
74 | OCC_238 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING IN LOC 74 TO 78 | 08/Jun/2026 | 10:00 | 08/Jun/2026 | 16:00 | RE LEDO | Requested | PLANNED |  | RQ32063 |  | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and kathalguri-Namsai-Tezu-Roing-Chapakhow-Rupai link
75 | OCC_238 | MEPTCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | Preventive maintenance work | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32115 |  | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Assam.
76 | OCC_238 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | TSECL | D | Routine Maintenance Work | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32039 |  | SD may be availed
77 | OCC_238 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | MEPTCL,AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 | AGM PANCHGRAM | Requested | PLANNED |  | RQ32081 |  | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya.
78 | OCC_238 | MEPTCL | LUMSNONG - 132KV - BUS 1 | MEPTCL | D | Preventive maintenance work | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32114 |  | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Assam. | need to be kept in PPT
79 | OCC_238 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | POWERGRID | D | AMP OF BAY EQUIPMENTS at Silchar SS | 08/Jun/2026 | 8:00 | 08/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32143 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
80 | OCC_238 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 08/Jun/2026 | 09:00 | 08/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32144 |  | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 2, 3 and 4.
81 | OCC_238 | POWERGRID | MAIN BAY (122) OF 220KV/132KV BALIPARA-ICT-1 @BALIPARA - 132KV | POWERGRID | D | For panel cutting and placing the relay in panel with cable laying) to facilate replacment of Static relay by Numerical Relay( P141) and testing of numerical relay . ICT -1 shall remain charged throughb TBC Bay . | 08/Jun/2026 | 08:00 | 08/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32189 |  | SD may be availed subject to no outage of elements. ICT-1 may be charged through transfer bus
82 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 08/Jun/2026 | 07:00 | 08/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32031 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
83 | OCC_238 | Arunachal Pradesh | 132KV-LEKHI-NIRJULI-1 | POWERGRID,DOP,ARUNACHAL PRADESH | C | Removal of Line bay jumpering and other necessary work | 08/Jun/2026 | 06:00 | 11/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32222 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare,132kV Panyor – Itanagar and 132kV Panyor – Lekhi. 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 • Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period during the off peak hours. The sequence of Unit synchronisation are as follows: Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the off peak hours of shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
84 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 1 | DOP,ARUNACHAL PRADESH | D | Modification of switching arrangement | 08/Jun/2026 | 06:00 | 08/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32220 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
85 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 2 | DOP,ARUNACHAL PRADESH | D | Modification of switching Arrangement | 08/Jun/2026 | 06:00 | 08/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32221 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
86 | OCC_238 | POWERGRID | TRANSFER BUS COUPLER BAY (106) OF SALAKATI - 132KV - BUS 1 AND SALAKATI - 132KV - BUS 2 @SALAKATI - 132KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 09/Jun/2026 | 15:00 | 09/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32191 |  | S/d may be availed
87 | OCC_238 | POWERGRID | 132 KV GELEPHU BAY (110) AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 09/Jun/2026 | 10:00 | 09/Jun/2026 | 13:00 |  | Requested | PLANNED |  | RQ32193 |  | SD may be availed subject to no outage of element .Intimation to NLDC.
88 | OCC_238 | POWERGRID | 400 KV BALIPARA 4 BAY (WITH 63 MVAR LINE REACTOR) AT BONGAIGAON | POWERGRID | D | AMP WORKS . Note - 400 KV Balipara -4 Bay at Bongaigaon SS is Bay 418 as per actual SLD . | 09/Jun/2026 | 09:30 | 09/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32195 |  | SD may be availed Subject to the main bay of Alipurduar II@Bongaigaon and tie bay of Alipurduar II & Balipara IV
89 | OCC_238 | POWERGRID | 220 KV MISA 2 BAY AT SAMAGURI | POWERGRID | C | CB Mechanism overhauling works. It may be noted that Line was charged through Bus coupler. | 09/Jun/2026 | 8:00 | 11/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32194 |  | Sd may be aviled subject to no outage of elements. | 09/Jun/2026 to 11/Jun/2026 08:00 to 16:00
90 | OCC_238 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | AEGCL | D | ROUTINE TESTING | 09/Jun/2026 | 09:00 | 09/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32060 |  | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period. | need to include in OCC discussion
91 | OCC_238 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 09/Jun/2026 | 09:00 | 09/Jun/2026 | 16:00 | AGM RANGIA | Requested | PLANNED |  | RQ32074 |  | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
92 | OCC_238 | POWERGRID | 132KV-BADARPUR-JIRIBAM(PG)-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM | 09/Jun/2026 | 09:00 | 09/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32145 |  | Shutdown may be availed
93 | OCC_238 | POWERGRID | 400KV-BALIPARA-BONGAIGAON-2 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Jun/2026 | 09:00 | 09/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32146 |  | Sd may be availed subject to the availability of 400kV Balipara-Bongaiagon 1, 3 and 4
94 | OCC_238 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-1 | NAGALAND,DOP | D | Vegetation Clearance | 09/Jun/2026 | 09:00 | 09/Jun/2026 | 15:00 |  | Requested | PLANNED |  | RQ32129 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokhoa-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
95 | OCC_238 | Arunachal Pradesh | 220KV-AGBPP-DEOMALI-1 | DOP,ARUNACHAL PRADESH | D | AMP | 09/Jun/2026 | 08:30 | 09/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32128 |  | SD may be availed. Deomali and Khonsa substation will under dark. Intimation to neepco | PPT
96 | OCC_238 | POWERGRID | MAIN BAY (124) OF 220KV/132KV BALIPARA-ICT-2 @BALIPARA - 132KV | POWERGRID | D | For panel cutting and placing the relay in panel with cable laying) to facilate replacment of Static relay by Numerical Relay( P141) and testing of numerical relay . ICT -2 shall remain charged throughb TBC Bay . | 09/Jun/2026 | 08:00 | 09/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32192 |  | SD may be availed subject to no outage of elements. ICT-2 may be charged through transfer bus
97 | OCC_238 | POWERGRID | 132KV-KARIMGANJ (AS)-KUMARGHAT-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Jun/2026 | 08:00 | 09/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32147 |  | Sd may be availed subject to the availability of 132kV Badarpur-Karimganj link
98 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 09/Jun/2026 | 07:00 | 09/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32032 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
99 | OCC_238 | NEEPCO | MONARCHAK(THERMAL) - GTG 1 | NEEPCO | C | Air filter replacement, Compressor offline water wash, and other electrical maintenance works | 09/Jun/2026 | 00:00 | 13/Jun/2026 | 23:59 | Planned Shutdown | Requested | PLANNED |  | RQ32007 |  | Sd may be availed. Consent from Tripura is required | Sd deferred and may be availed subject to the restoration of Palatana
100 | OCC_238 | NEEPCO | MONARCHAK(THERMAL) - UNIT 2 | NEEPCO | C | Air filter replacement, Compressor offline water wash, and other electrical maintenance works | 09/Jun/2026 | 00:00 | 13/Jun/2026 | 23:59 | Planned Shutdown | Requested | PLANNED |  | RQ32008 |  | Sd may be availed. Consent from Tripura is required | Sd deferred and may be availed subject to the restoration of Palatana
101 | OCC_238 | POWERGRID | 132KV MAIN BAY OF 220KV/132KV SALAKATI-ICT-3 @SALAKATI - 132KV | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 10/Jun/2026 | 14:00 | 10/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32196 |  | SD may be availed subject to no outage of elements. Tie bay must be in service | 14:00-16:00
102 | OCC_238 | POWERGRID | 220KV/132KV BALIPARA-ICT-2 | POWERGRID | D | Replacment of LBB Static relay with Numerical Relay( P141) and testing of numerical relay with same settings for back Trip testing | 11/Jun/2026 | 8:00 | 11/Jun/2026 | 13:00 |  | Requested | PLANNED |  | RQ32170 |  | SD may be availed subject to availability of 220/132kV ICT-1 at Balipara S/S and 132kV Kameng-Khupi-Tenga-Balipara link. NERPC Approval is required before charging of the line | 11/Jun/2026 08:00 to 13:00
103 | OCC_238 | POWERGRID | 132 KV, 50 MVA ICT 2 BAY AT SALAKATI | POWERGRID | D | SF6 quality testing of CB . Element shall remain charged though TBC bay | 10/Jun/2026 | 9:00 | 10/Jun/2026 | 12:00 |  | Requested | PLANNED |  | RQ32197 |  | SD may be availed subject to no outage of element | 09:00-12:00
104 | OCC_238 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | MEGHALAYA | D | Tightening of nuts and bolts between Tower Location 108 to 106. | 10/Jun/2026 | 10:00 | 10/Jun/2026 | 15:00 | Avail | Requested | PLANNED |  | RQ32209 |  | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
105 | OCC_238 | POWERGRID | 132KV/33KV NIRJULI-ICT-2 | POWERGRID | D | AMP works | 10/Jun/2026 | 09:00 | 10/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32166 |  | Sd may be subject to the consent from AP | PPT
106 | OCC_238 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 10/Jun/2026 | 09:00 | 10/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32089 |  | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
107 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | TSECL | D | Routine Maintenance Work | 10/Jun/2026 | 09:00 | 10/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32040 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
108 | OCC_238 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-1 | NAGALAND,DOP | D | Vegetation Clearance | 10/Jun/2026 | 09:00 | 10/Jun/2026 | 15:00 |  | Requested | PLANNED |  | RQ32130 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokhoa-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid. | PPT
109 | OCC_238 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | ARUNACHAL PRADESH | D | AMP | 10/Jun/2026 | 8:00 | 10/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32014 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. | 08:00-16:00 | Date change
110 | OCC_238 | POWERGRID | 220KV/132KV BALIPARA-ICT-1 | NEEPCO | D | Replacment of LBB Static relay with Numerical Relay( P141) and testing of numerical relay with same settings for back Trip testing | 10/Jun/2026 | 08:00 | 10/Jun/2026 | 13:00 |  | Requested | PLANNED |  | RQ32169 |  | SD may be availed subject to availability of 220/132kV ICT-2 at Balipara S/S and 132kV Kameng-Khupi-Tenga-Balipara link. NERPC Approval is required before charging of the line
111 | OCC_238 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 65 | 10/Jun/2026 | 08:00 | 10/Jun/2026 | 16:00 | AGM MNI & AGM T&T NGN | Requested | PLANNED |  | RQ32103 |  | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
112 | OCC_238 | POWERGRID | 132KV-SILCHAR-HAILAKANDI-2 | POWERGRID | D | AMP of Bay and line equipments at Halakandi SS | 10/Jun/2026 | 08:00 | 10/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32148 |  | Shutdown may be availed subject to availability of 132KV-SILCHAR-HAILAKANDI-1 and 132kv Panchgram-Hailakandi. Consent from Assam
113 | OCC_238 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance Work | 10/Jun/2026 | 08:00 | 10/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32116 |  | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
114 | OCC_238 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance Work | 11/Jun/2026 | 08:00 | 11/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32117 |  | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing. | 11/Jun/2026
115 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 10/Jun/2026 | 07:00 | 10/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32033 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
116 | OCC_238 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | AEGCL | D | CORRIDOR CLEANING LOC 1-47 | 11/Jun/2026 | 10:00 | 11/Jun/2026 | 16:00 | AGM TINSUKIA | Requested | PLANNED |  | RQ32108 |  | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO | PPT
117 | OCC_238 | POWERGRID | 400 KV BALIPARA 3 BAY (WITH 63 MVAR LINE REACTOR) (418) AT BONGAIGAON | POWERGRID | D | AMP WORKS . Note - 400 KV Balipara -3 Bay at Bongaigaon SS is Bay 419 as per actual SLD . | 11/Jun/2026 | 09:30 | 11/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32198 |  | SD may be availed subject to the availability of main bay of 400kV Azara@Bongaigaon and tie bay of Balipara III & Azara
118 | OCC_238 | POWERGRID | 220KV/132KV BALIPARA-ICT-1 | NEEPCO | D | For Re Trip testing after Replacment of LBB Static relay with Numerical Relay( P141) and testing of numerical relay | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 14:00 |  | Requested | PLANNED |  | RQ32164 |  | Sd may be availed subject to the availability of 132kv Kameng-Khupi-Tenga link. Consent from AP is required | 12/Jun/2026
119 | OCC_238 | POWERGRID | 220KV/132KV BALIPARA-ICT-2 | POWERGRID | D | For Re Trip testing after Replacment of LBB Static relay with Numerical Relay( P141) and testing of numerical relay | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 14:00 |  | Requested | PLANNED |  | RQ32165 |  | Sd may be availed subject to the availability of 132kv Kameng-Khupi-Tenga link. Consent from AP is required | 12/Jun/2026
120 | OCC_238 | POWERGRID | BALIPARA - 132KV - BUS 1 | POWERGRID | D | For Re Trip testing after Replacment of LBB Static relay with Numerical Relay( P141) and testing of numerical relay in ICT-1&2 | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 14:00 |  | Requested | PLANNED |  | RQ32212 |  | Sd may be availed subject to the availability of 132kv Kameng-Khupi-Tenga link. Consent from AP is required | 12/Jun/2026
121 | OCC_238 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | AEGCL | D | CORRIDOR CLEANING | 16/Jun/2026 | 09:00 | 16/Jun/2026 | 16:00 | RE GLG | Requested | PLANNED |  | RQ32070 |  | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service. | 16/Jun/2026
122 | OCC_238 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | AEGCL | D | PREVENTIVE MAINTENANCE | 11/Jun/2026 | 09:00 | 11/Jun/2026 | 16:00 | AGM RANGIA | Requested | PLANNED |  | RQ32075 |  | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
123 | OCC_238 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 11/Jun/2026 | 09:00 | 11/Jun/2026 | 16:00 | RE RUPAI | Requested | PLANNED |  | RQ32109 |  | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link
124 | OCC_238 | POWERGRID | 132KV-BALIPARA-KHUPI-1 | NEEPCO,ARUNACHAL PRADESH | D | Replacment of Static relay by Numerical Relay( P141) and testing of numerical relay | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32149 |  | Sd may be availed subject to the availability of 132kv Kameng-Khupi-Tenga link. Consent from AP is required | 12/Jun/2026
125 | OCC_238 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-1 | NAGALAND,DOP | D | Vegetation Clearance | 11/Jun/2026 | 09:00 | 11/Jun/2026 | 15:00 |  | Requested | PLANNED |  | RQ32131 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokhoa-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
126 | OCC_238 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 11/Jun/2026 | 08:30 | 11/Jun/2026 | 16:00 | AGM T&T GOALPARA & AGM SSJI | Requested | PLANNED |  | RQ32091 |  | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
127 | OCC_238 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 66 TO 135 | 11/Jun/2026 | 08:00 | 11/Jun/2026 | 16:00 | AGM MNI & AGM T&T NGN | Requested | PLANNED |  | RQ32104 |  | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
128 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 11/Jun/2026 | 07:00 | 11/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32034 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
129 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 1 | DOP,ARUNACHAL PRADESH | D | Modification of switching arrangement | 11/Jun/2026 | 07:00 | 11/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32223 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
130 | OCC_238 | Arunachal Pradesh | LEKHI - 132KV - BUS 2 | DOP,ARUNACHAL PRADESH | D | Modification of switching Arrangment | 11/Jun/2026 | 07:00 | 11/Jun/2026 | 09:00 | As per 233th OCCM Discussion | Requested | PLANNED |  | RQ32224 |  | SD may be availed subject to the following study: 1. Availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar 2. 132kV Panyor Bus to be operated in split mode as follows: • ICT 1 & II and Unit 1, 2 to be kept in Bus 1 •Unit 3, 132kV Panyor – Ziro, 132kV Panyor – Pare and 132kV Panyor – Itanagar in Bus 2 3. One unit of Pare and one unit of Panyor is to be scheduled during the shutdown period. The sequence of Unit synchronisation are as follows: • Synchronising of Pare unit followed by synchronisation of Panyor unit in Bus 1, and then opening of Bus coupler at Panyor to split the bus. 4. If 3 unit of Panyor is scheduled during the shutdown then generation of Panyor to be restricted to 390 MW, with Unit 3 maximum generation of 120 MW 5. If scheduling of Pare and Panyor is not possible during the shutdown period, then Combined loading of AP capital and Gohpur to restricted to 165 MW. Consent from NEEPCO is required | SD is already taken under POST OCC
131 | OCC_238 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING IN LOC 95 TO 101 | 12/Jun/2026 | 10:00 | 12/Jun/2026 | 16:00 | RE LEDO | Requested | PLANNED |  | RQ32061 |  | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link and kathalguri-Namsai-Tezu-Roing link
132 | OCC_238 | POWERGRID | MAIN BAY (2) OF 400KV-SILCHAR-IMPHAL(PG)-2 @IMPHAL(PG) - 400KV | POWERGRID | D | AMP of bay equipment | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 14:00 |  | Requested | PLANNED |  | RQ32199 |  | SD may be availed subject to no outage of elements
133 | OCC_238 | Arunachal Pradesh | 132KV-ALONG-BASAR-1 | ARUNACHAL PRADESH | D | AMP | 13/Jun/2026 | 09:00 | 13/Jun/2026 | 17:30 |  | Requested | PLANNED |  | RQ32011 |  | Sd may be availed subject to availability of 132kV Panyor-ziro-daprorijo-along link and 132kv Roing-Pasighat-Basar link | 13/Jun/2026
134 | OCC_238 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | AEGCL | D | CORRIDOR CLEANING LOC 1 TO 108 | 12/Jun/2026 | 09:00 | 12/Jun/2026 | 16:00 | RE RUPAI | Requested | PLANNED |  | RQ32110 |  | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link. & 132 Rupai -Margarita -Tinsukia link | SD deferred as already applied on 11-June-2026.
135 | OCC_238 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 400 TO 368 | 12/Jun/2026 | 08:30 | 12/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32095 |  | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link. SPS regarding tripping of Azara-Sarusajai D/C needs to be turned ON if loading exceeds 220MW.
136 | OCC_238 | POWERGRID | MARIANI (PG) - 220KV - BUS 1 | POWERGRID | D | AMP works | 13/Jun/2026 | 08:00 | 13/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32211 |  | SD may be availed subject to the availability of other bus and all the elements needs to be transferred to other bus, Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220/132kv ICTs at Mariani(AS), 220kv Mariani(AS)-Samaguri, 220kV Mariani(PG)-Kathalguri-Mariani(AS) link, 220kv AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link, 220kV Kathalguri-Namsai D/C needs to be maintained. Upper Assam load needs to be maintained under 550MW if generation in Upper Assam is 290 MW (including AGBPP generation as 135MW). For every 10MW increase in generation 2 MW load can be increased. Dimapur-Doyang-Mokokchung(NL)-Mokokchung, 132kv Kohima-Meluri-Tuensanf-Mokokchung(NL)-Mokokchung link also needs to be present | 13/Jun/2026
137 | OCC_238 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING 135 TO 194 | 12/Jun/2026 | 08:00 | 12/Jun/2026 | 16:00 | AGM MNI & AGM T&T NGN | Requested | PLANNED |  | RQ32105 |  | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
138 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 12/Jun/2026 | 07:00 | 12/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32035 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
139 | OCC_238 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Routine Maintenance Work | 13/Jun/2026 | 09:00 | 13/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32041 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
140 | OCC_238 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | MEPTCL | D | Replacement of broken disc and jumper repairing at Loc 54. | 13/Jun/2026 | 08:00 | 13/Jun/2026 | 15:00 | Avail | Requested | PLANNED |  | RQ32113 |  | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Intimation to Assam
141 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 13/Jun/2026 | 07:00 | 13/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32036 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
142 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 14/Jun/2026 | 07:00 | 14/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32037 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
143 | OCC_238 | Arunachal Pradesh | 132KV-TENGA-KHUPI-1 | ARUNACHAL PRADESH | D | Vegetation Clearance | 14/Jun/2026 | 07:00 | 14/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32124 |  | SD may be availed subject to the availability of 132kv Kameng-Khupi and 132kv Balipara-Tenga.
144 | OCC_238 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 75 | 15/Jun/2026 | 09:00 | 15/Jun/2026 | 16:00 | AGM T&T NGN | Requested | PLANNED |  | RQ32099 |  | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
145 | OCC_238 | Arunachal Pradesh | BASAR - 132KV - BUS 1 | ARUNACHAL PRADESH | D | AMP | 15/Jun/2026 | 8:00 | 15/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32017 |  | SD may be availed subject to availability of Ranganadi-ziro-along and pasighat-roing-tzeu-namsai-kathalguri link and roing-chapakhowa-rupai-tinsukia link | 08:00-16:00
146 | OCC_238 | Arunachal Pradesh | BASAR - 132KV - BUS 2 | ARUNACHAL PRADESH | D | AMP | 15/Jun/2026 | 8:00 | 15/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32016 |  | SD may be availed subject to availability of Ranganadi-ziro-along and pasighat-roing-tzeu-namsai-kathalguri link and roing-chapakhowa-rupai-tinsukia link | 08:00-16:00
147 | OCC_238 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 15/Jun/2026 | 08:30 | 15/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32093 |  | S/D may be availed.400kv Bongaigaon-Mirza, 400/220kV ICTs at Mirza, 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
148 | OCC_238 | POWERGRID | MARIANI (PG) - 220KV - BUS 2 | POWERGRID | D | AMP works | 15/Jun/2026 | 08:00 | 15/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32213 |  | SD may be availed subject to the availability of other bus and all the elements needs to be transferred to other bus, Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220/132kv ICTs at Mariani(AS), 220kv Mariani(AS)-Samaguri, 220kV Mariani(PG)-Kathalguri-Mariani(AS) link, 220kv AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link, 220kV Kathalguri-Namsai D/C needs to be maintained. Upper Assam load needs to be maintained under 550MW if generation in Upper Assam is 290 MW (including AGBPP generation as 135MW). For every 10MW increase in generation 2 MW load can be increased. Dimapur-Doyang-Mokokchung(NL)-Mokokchung, 132kv Kohima-Meluri-Tuensanf-Mokokchung(NL)-Mokokchung link also needs to be present
149 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | TSECL | D | Installation of transmission line Surge Arrester | 15/Jun/2026 | 07:00 | 15/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32038 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
150 | OCC_238 | POWERGRID | 400 KV BISWANATH CHARIALI 2 MAIN BAY(WITH 50 MVAR LINE REACTOR)(407) AT BALIPARA | POWERGRID | C | CB Mechanism overhauling works | 16/Jun/2026 | 09:00 | 18/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32200 |  | Sd may be availed subject to no outage of elements
151 | OCC_238 | POWERGRID | 400 KV, 200 MVA ICT 1 MAIN BAY AT SILCHAR | POWERGRID | D | AMP works | 16/Jun/2026 | 09:00 | 16/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32201 |  | SD may be availed subject to no outage of elements.
152 | OCC_238 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 16/Jun/2026 | 09:00 | 16/Jun/2026 | 16:00 | AGM RANGIA | Requested | PLANNED |  | RQ32076 |  | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
153 | OCC_238 | AEGCL | 220KV-AGIA-BTPS-1 | AEGCL | D | CORRIDOR CLEANING | 29/Jun/2026 | 09:00 | 29/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32086 |  | S/D may be availed subject to availability of 220kV Agia-BTPS 2 line, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s should be kept in service. | 29/Jun/2026
154 | OCC_238 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 76 TO 155 | 16/Jun/2026 | 09:00 | 16/Jun/2026 | 16:00 | AGM T&T NGN | Requested | PLANNED |  | RQ32100 |  | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
155 | OCC_238 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | TSECL | D | Routine Maintenance Work | 16/Jun/2026 | 8:00 | 16/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32043 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
156 | OCC_238 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 368 TO 329 | 16/Jun/2026 | 08:30 | 16/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32096 |  | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link. SPS regarding tripping of 220kv Azara-Sarusajai D/C needs to be kept on if loading exceeds 220MW.
157 | OCC_238 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 125 to 123. | 17/Jun/2026 | 10:00 | 17/Jun/2026 | 15:00 | Avail | Requested | PLANNED |  | RQ32210 |  | SD may be availed subject to the availability of 220KV-NEW SHILLONG-MAWNGAP-1
158 | OCC_238 | AEGCL | 220KV-TINSUKIA-NTPS-1 | ASSAM | D | CORRIDOR CLEANING LOC 1-68 | 17/Jun/2026 | 10:00 | 17/Jun/2026 | 16:00 | AGM TINSUKIA | Requested | PLANNED |  | RQ32072 |  | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
159 | OCC_238 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 17/Jun/2026 | 09:00 | 17/Jun/2026 | 16:00 | RE BKJ | Requested | PLANNED |  | RQ32084 |  | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service.
160 | OCC_238 | AEGCL | 220KV-AGIA-BTPS-2 | AEGCL | D | CORRIDOR CLEANING | 19/Jun/2026 | 09:00 | 19/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32088 |  | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. | 19/Jun/2026
161 | OCC_238 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 01 TO 75 | 17/Jun/2026 | 09:00 | 17/Jun/2026 | 16:00 | AGM T&T NGN | Requested | PLANNED |  | RQ32101 |  | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
162 | OCC_238 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | TSECL | D | Routine Maintenance Work | 17/Jun/2026 | 09:00 | 17/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32042 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
163 | OCC_238 | POWERGRID | BONGAIGAON - 400KV B/R 3 | POWERGRID | C | AMP works | 17/Jun/2026 | 09:00 | 17/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32217 |  | SD may be availed
164 | OCC_238 | POWERGRID | BONGAIGAON - 400KV B/R 4 | POWERGRID | C | AMP works | 17/Jun/2026 | 09:00 | 17/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32218 |  | SD may be availed
165 | OCC_238 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | AEGCL | D | PREVENTIVE MAINTENANCE | 18/Jun/2026 | 09:00 | 18/Jun/2026 | 16:00 | AGM RANGIA | Requested | PLANNED |  | RQ32077 |  | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
166 | OCC_238 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 76 TO 155 | 18/Jun/2026 | 09:00 | 18/Jun/2026 | 16:00 | AGM T&T NGN | Requested | PLANNED |  | RQ32102 |  | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C and 220kV Samaguri - Mariani (AS)
167 | OCC_238 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | MEPTCL | D | Maintenance Work | 18/Jun/2026 | 08:00 | 18/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32118 |  | Sd may be availed subject to the availability of 220kV Killing-Misa 2, 400/220 KV ICT 1 and 2 at Killing.
168 | OCC_238 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | MEPTCL | D | Maintenance Work | 19/Jun/2026 | 08:00 | 19/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32119 |  | Sd may be availed subject to the availability of 220kV Killing-Misa 1, 400/220 KV ICT 1 and 2 at Killing. | 19/Jun/2026
169 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 18/Jun/2026 | 07:00 | 18/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32044 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
170 | OCC_238 | Arunachal Pradesh | 132KV-KAMENG-KHUPI-1 | NEEPCO,ARUNACHAL PRADESH | D | Vegetation Clearance | 18/Jun/2026 | 07:00 | 18/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32126 |  | SD may be availed subject to availability of 132kv Balipara-Tenga-Khupi link. Intimation to NEEPCO
171 | OCC_238 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | AEGCL | D | CORRIDOR CLEANING IN LOC 101 TO 105 | 19/Jun/2026 | 10:00 | 19/Jun/2026 | 16:00 | RE LEDO | Requested | PLANNED |  | RQ32062 |  | S/D may be availed subject to the availability of 132kV Tinsukia_Rupai and 132kV Tinsukia Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
172 | OCC_238 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 19/Jun/2026 | 09:00 | 19/Jun/2026 | 16:00 | RE BKJ | Requested | PLANNED |  | RQ32069 |  | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
173 | OCC_238 | POWERGRID | MAIN BAY (410) OF 400KV-NEW KOHIMA-MARIANI (PG)-1 @MARIANI (PG) - 400KV | POWERGRID | D | For checking & attending SF6 leakage in Main Bay R-phase CB | 19/Jun/2026 | 08:00 | 19/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32180 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
174 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 19/Jun/2026 | 07:00 | 19/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32045 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
175 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 20/Jun/2026 | 07:00 | 20/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32046 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
176 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 21/Jun/2026 | 07:00 | 21/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32047 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
177 | OCC_238 | Arunachal Pradesh | 132KV-KAMENG-KHUPI-1 | NEEPCO,ARUNACHAL PRADESH | D | Vegetation Clearance | 21/Jun/2026 | 07:00 | 21/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32127 |  | SD may be availed subject to availability of 132kv Balipara-Tenga-Khupi link. Intimation to NEEPCO
178 | OCC_238 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | INDIGRID | D | Routine Maintenance Work | 22/Jun/2026 | 09:00 | 22/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32057 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
179 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 22/Jun/2026 | 07:00 | 22/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32048 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
180 | OCC_238 | POWERGRID | 400 KV BISWANATH CHARIALI 3 MAIN BAY (415) AT BALIPARA | POWERGRID | C | CB Mechanism overhauling works.Note - 400 KV BNC#3 Main Bay at Balipara SS is 413 Bay as per SLD of Balipara SS . | 23/Jun/2026 | 09:00 | 25/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32202 |  | SD may be availed, BNC 3 shares dia with Bongaigaon 1
181 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 23/Jun/2026 | 07:00 | 23/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32049 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
182 | OCC_238 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | MEHGALAYA | D | Tightening of nuts and bolts between Tower Location 122 to 120. | 24/Jun/2026 | 10:00 | 24/Jun/2026 | 15:00 | Avail | Requested | PLANNED |  | RQ32216 |  | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
183 | OCC_238 | POWERGRID | 400 KV, 50 MVAR BUS REACTOR 2 BAY AT BONGAIGAON | POWERGRID | D | AMP works | 24/Jun/2026 | 09:30 | 24/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32203 |  | SD may be availed
184 | OCC_238 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | POWERGRID | D | Warranty testing of GIS Bays at Dimapur SS | 24/Jun/2026 | 08:00 | 24/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32171 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
185 | OCC_238 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 24/Jun/2026 | 08:00 | 24/Jun/2026 | 16:00 | AGM MNI | Requested | PLANNED |  | RQ32065 |  | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
186 | OCC_238 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | MEGHALAYA | D | Maintenance Work | 27/Jun/2026 | 08:00 | 27/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32120 |  | SD may be availed subject to availability of 220kV Mawngap - Killing 2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW | 27/Jun/2026
187 | OCC_238 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | MEGHALAYA | D | Maintenance Work | 27/Jun/2026 | 08:00 | 27/Jun/2026 | 16:00 | Avail | Requested | PLANNED |  | RQ32121 |  | SD may be availed subject to availability of 220kV Mawngap - Killing 2, 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW | 27/Jun/2026
188 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 24/Jun/2026 | 07:00 | 24/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32050 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
189 | OCC_238 | AEGCL | 220KV-TINSUKIA-NRPP-1 | ASSAM | D | CORRIDOR CLEANING LOC 70-136 | 25/Jun/2026 | 10:00 | 25/Jun/2026 | 16:00 | AGM TINSUKIA | Requested | PLANNED |  | RQ32073 |  | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
190 | OCC_238 | AEGCL | 220KV-AGIA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING | 25/Jun/2026 | 09:00 | 25/Jun/2026 | 16:00 | AGM T&T GOALPARA | Requested | PLANNED |  | RQ32090 |  | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
191 | OCC_238 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | TSECL | D | Routine Maintenance Work | 25/Jun/2026 | 09:00 | 25/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32058 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam | PPT
192 | OCC_238 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | POWERGRID | D | Warranty testing of GIS Bays at Dimapur SS | 25/Jun/2026 | 08:00 | 25/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32172 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
193 | OCC_238 | AEGCL | 220KV-NTPS-AMGURI-1 | AEGCL | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 26/Jun/2026 | 08:00 | 26/Jun/2026 | 16:00 | AGM MNI | Requested | PLANNED |  | RQ32066 |  | S/D may be availed subject to availability of 220 k Mariani-Amguri line. | 26/Jun/2026
194 | OCC_238 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-1 | PGCB,POWERGRID | D | AMP works | 25/Jun/2026 | 7:00 | 25/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32150 |  | SD may be availed subject to the availabilityof 132kV Surajmaninagar-Comilla 2, NLDC consent is required
195 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 25/Jun/2026 | 07:00 | 25/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32051 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
196 | OCC_238 | POWERGRID | 400 KV ALIPURDUAR 1 BAY (415) AT BONGAIGAON | POWERGRID | D | AMP works | 26/Jun/2026 | 09:30 | 26/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32204 |  | Sd may be availed subject to no outage of element. Intimation to NLDC
197 | OCC_238 | POWERGRID | TIE BAY () OF 400KV-AZARA-SILCHAR AND 400KV/132KV SILCHAR-ICT-1 @SILCHAR - 400KV | POWERGRID | D | AMP works | 26/Jun/2026 | 09:00 | 26/Jun/2026 | 17:00 |  | Requested | PLANNED |  | RQ32205 |  | SD may be availed subject to no outage of element
198 | OCC_238 | AEGCL | 220KV-AGIA-AZARA-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 26/Jun/2026 | 08:30 | 26/Jun/2026 | 16:00 | AGM T&T GOALPARA & AGM SSJI | Requested | PLANNED |  | RQ32092 |  | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
199 | OCC_238 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-2 | PGCB,POWERGRID | D | AMP works | 26/Jun/2026 | 7:00 | 26/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32151 |  | SD may be availed subject to the availabilityof 132kV Surajmaninagar-Comilla 1, NLDC consent is required
200 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 26/Jun/2026 | 07:00 | 26/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32052 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
201 | OCC_238 | POWERGRID | 132KV-AGARTALA (79 TILLA)-AGTCCPP-1 | POWERGRID | D | AMP OF BAY EQUIPMENTS | 27/Jun/2026 | 08:00 | 27/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32152 |  | SD may be availed subject to the availabitiy of 132kV Agartala-AGTCCPP-2, 132kV AGTCPP-PK Bari D/C. Intimation to NEEPCO
202 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 27/Jun/2026 | 07:00 | 27/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32053 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
203 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 28/Jun/2026 | 07:00 | 28/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32054 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
204 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 29/Jun/2026 | 07:00 | 29/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32055 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
205 | OCC_238 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | TSECL | D | Routine Maintenance Work | 30/Jun/2026 | 09:00 | 30/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32059 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link | SD may be availed after restoration of 132kV 132KV-AGARTALA (79 TILLA)-ROKHIA-2
206 | OCC_238 | AEGCL | 220KV-AZARA-BOKO-1 | AEGCL | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE | 30/Jun/2026 | 08:30 | 30/Jun/2026 | 16:00 | AGM SARUSAJAI | Requested | PLANNED |  | RQ32094 |  | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
207 | OCC_238 | POWERGRID | 132KV-AGTCCPP-KUMARGHAT-1 | POWERGRID | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 30/Jun/2026 | 08:00 | 30/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32153 |  | Sd may be availed subject to the availability of Badarpur-karimganj-Kumarghat link and PK Bari-Kumarghat. Intimation to NEEPCO
208 | OCC_238 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | TSECL | D | Installation of transmission line Surge Arrester | 30/Jun/2026 | 07:00 | 30/Jun/2026 | 16:00 |  | Requested | PLANNED |  | RQ32056 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link. Annexure B7 to be submitted to NERLDC FTC before final charging of element.
209 | OCC_238 | NEEPCO | AGBPP - GTG 1 | TSECL | C | R&M works | 15/Jun/2026 | 07:00 | 2026-07-09 | 16:00 |  | Requested | PLANNED |  | RQ32056 |  | S/D may be availed. Consent from Beneficiaries is required