## Sheet1
Sl no. | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Study remarks
1 | OCC_239 | NTPC | BGTPP - 400KV - BUS 1 | C | reason | 01/Jul/2026 | 09:00 | 01/Jul/2026 | 18:00 |  | SD deferred
2 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI GIS-2 | D | Rectification of Earthing of NGR | 01/Jul/2026 | 09:00 | 01/Jul/2026 | 14:00 |  | SD may be availed Intimation to NHPC
3 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Balipara TLM | 01/Jul/2026 | 8:00 | 01/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-BALIPARA-1, 2 & 4.
4 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-BALIPARA-4 | D | Shutdown of Circuit-4 not required. AR in Non-auto mode of circuit-4 for replacement of insulator for circuit-4. | 01/Jul/2026 | 8:00 | 01/Jul/2026 | 16:00 | Shutdown not required. Only AR Non-Auto required for circuit-04 while working in Circuit-03 | A/R may be kept in Non-Auto mode
5 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-2 L/R@ BISWANATH CHARIALI - 400KV | D | Rectification of Earthing of NGR | 01/Jul/2026 | 09:00 | 01/Jul/2026 | 14:00 |  | SD may be availed.
6 | OCC_239 | POWERGRID | 400 KV, 315 MVA ICT 3 MAIN BAY AT SILCHAR | D | AMP OF BAY EQUIPMENTS | 01/Jul/2026 | 08:00 | 01/Jul/2026 | 17:00 |  | SD may be availed subject to no outage of ICT-3
7 | OCC_239 | POWERGRID | NAMSAI - 132KV B/R 1 | D | AMP works of Reactor | 01/Jul/2026 | 08:00 | 01/Jul/2026 | 14:00 |  | SD may be availed
8 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 01/Jul/2026 | 07:00 | 01/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
9 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 01/Jul/2026 | 07:00 | 01/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
10 | OCC_239 | NEEPCO | AGBPP - STG 2 | C | Major overhauling of generator and exciter | 01/Jul/2026 | 00:00 | 28/Jul/2026 | 00:00 |  | SD won't be availed by NEEPCO due to man-power issue
11 | OCC_239 | NTPC | BGTPP - 400KV - BUS 2 | C | reason | 02/Jul/2026 | 09:00 | 04/Jul/2026 | 18:00 |  | SD deferred
12 | OCC_239 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 02/Jul/2026 | 09:00 | 02/Jul/2026 | 15:00 | AGM PANCHGRAM | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
13 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Routine Maintenance Work | 02/Jul/2026 | 09:00 | 02/Jul/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
14 | OCC_239 | POWERGRID | 132KV-SILCHAR-HAILAKANDI-1 | D | Replacment of insulator due to flashover dated at Loc- 21 by Silchar TLM. | 02/Jul/2026 | 7:00 | 02/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Hailakandi(Assam)-Silchar-Hailakandi ckt 2 and Panchgram-Hailakandi link. Consent from Assam
15 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 02/Jul/2026 | 07:00 | 02/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
16 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 02/Jul/2026 | 07:00 | 02/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
17 | OCC_239 | POWERGRID | 400 KV ALIPURDUAR 2 BAY (416) AT BONGAIGAON | D | AMP OF BAY EQUPMENTS | 03/Jul/2026 | 8:00 | 03/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of tie bay of 400kV Alipurduar II & Balipara IV@Bongaigaon & Main bay of 400kV Balipara IV@Bongaigaon. Intimation to NLDC
18 | OCC_239 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING | 04/Jul/2026 | 7:00 | 04/Jul/2026 | 14:00 | AGM T& T GOALPARA | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 380 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
19 | OCC_239 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 03/Jul/2026 | 09:00 | 03/Jul/2026 | 16:00 | RE GLG | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
20 | OCC_239 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 03/Jul/2026 | 09:00 | 03/Jul/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool
21 | OCC_239 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Routine Maintenance Work | 03/Jul/2026 | 09:00 | 03/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
22 | OCC_239 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Jul/2026 | 08:00 | 03/Jul/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
23 | OCC_239 | POWERGRID | TIE BAY () OF 400KV/132KV SILCHAR-ICT-3 AND FUTURE @SILCHAR - 400KV | D | AMP OF BAY EQUIPMENTS | 03/Jul/2026 | 08:00 | 03/Jul/2026 | 17:00 |  | SD may be availed subject to availability of main bay of ICT-3 and 400/132kV ICT-1 &2 at Silchar.
24 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 03/Jul/2026 | 07:00 | 03/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
25 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 03/Jul/2026 | 07:00 | 03/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
26 | OCC_239 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING, LOC 36-82 | 04/Jul/2026 | 10:00 | 04/Jul/2026 | 16:00 | AGM TINSUKIA | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
27 | OCC_239 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Routine Maintenance Work | 01/Jul/2026 | 09:00 | 01/Jul/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
28 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Routine Maintenance Work | 04/Jul/2026 | 09:00 | 04/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV SM Nagar(ISTS)-Budhjungnagar and 132kV Surajmaninagar(TSECL)-Budhjungnagar
29 | OCC_239 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING, loc 1 TO 159 | 02/Jul/2026 | 08:30 | 02/Jul/2026 | 15:30 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Roing link. Intimation to AP and NERTS
30 | OCC_239 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 04/Jul/2026 | 08:30 | 04/Jul/2026 | 15:30 | AGM PANCHGRAM | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
31 | OCC_239 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation clearance | 04/Jul/2026 | 7:00 | 04/Jul/2026 | 16:00 | OK | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link , 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link and 132kV Rupai - Chapakhowa-Roing link
32 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 04/Jul/2026 | 08:00 | 04/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
33 | OCC_239 | POWERGRID | 132KV-KARIMGANJ (AS)-KUMARGHAT-1 | D | Replacment of insulator due to flashover dated 20.04.2026 at Loc: 174 by Silchar TLM . | 04/Jul/2026 | 7:00 | 04/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV Badarpur-Karimganj link. Consent from Assam
34 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 04/Jul/2026 | 07:00 | 04/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
35 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 04/Jul/2026 | 07:00 | 04/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
36 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Routine Maintenance Work | 05/Jul/2026 | 09:00 | 05/Jul/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
37 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 05/Jul/2026 | 08:00 | 05/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
38 | OCC_239 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation clearance | 05/Jul/2026 | 7:00 | 05/Jul/2026 | 16:00 | OK | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link, 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link and 132kV Tinsukai - Rupai - Chapakhowa - Roing link
39 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 05/Jul/2026 | 07:00 | 05/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
40 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 05/Jul/2026 | 07:00 | 05/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
41 | OCC_239 | AEGCL | LEDO - 132KV - BUS 1 | D | (MAIN BUS) REPAIRING OF 132kV BUT PT ISOLATOR | 05/Jul/2026 | 06:00 | 05/Jul/2026 | 09:00 | MAIN BUS, RE LEDO | SD may be availed subject to the availability of 132kV Tinsukia-Rupai-Chapakhowa-Roing link and 220kV Kathalguri-Namsai link and 132kV Namsai-Tezu-Roing link
42 | OCC_239 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 314-238 | 05/Jul/2026 | 06:00 | 05/Jul/2026 | 15:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
43 | OCC_239 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Routine Maintenance Work | 06/Jul/2026 | 09:00 | 06/Jul/2026 | 16:00 |  | SD may be availed
44 | OCC_239 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 06/Jul/2026 | 09:00 | 06/Jul/2026 | 16:00 | AGM T& T GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
45 | OCC_239 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Jul/2026 | 08:30 | 06/Jul/2026 | 15:30 | AGM PANCHGRAM | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
46 | OCC_239 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation clearance | 06/Jul/2026 | 7:00 | 06/Jul/2026 | 16:00 | OK | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
47 | OCC_239 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Jul/2026 | 08:00 | 06/Jul/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
48 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 06/Jul/2026 | 08:00 | 06/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
49 | OCC_239 | POWERGRID | 132KV-CHAPAKHOWA-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 06/Jul/2026 | 08:00 | 06/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-2, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
50 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 06/Jul/2026 | 7:00 | 06/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
51 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 06/Jul/2026 | 07:00 | 06/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
52 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 06/Jul/2026 | 07:00 | 06/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
53 | OCC_239 | AEGCL | 220KV-AGIA-AZARA-1 | D | CORRIDOR CLEANING | 07/Jul/2026 | 09:00 | 07/Jul/2026 | 16:00 | AGM T& T GOALPARA | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
54 | OCC_239 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING, loc 1 TO 108 | 03/Jul/2026 | 09:00 | 03/Jul/2026 | 15:30 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link & 132 Rupai -Margarita -Tinsukia link
55 | OCC_239 | POWERGRID | MAIN BAY (1) OF 400KV-SILCHAR-IMPHAL(PG)-1 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 07/Jul/2026 | 09:00 | 07/Jul/2026 | 14:00 |  | SD may be availed subject to the availability of tie bay fo 400kV Silchar-1 & 80 MVAr Bus Reactor-1@400kV Imphal and main bay of 80 MVAr Bus Reactor-1@400kV Imphal
56 | OCC_239 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Jul/2026 | 08:30 | 07/Jul/2026 | 15:30 | AGM PANCHGRAM | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, and 220kV Mawngap - Killing D/C shall be kept in service. Consent from Meghalaya.
57 | OCC_239 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | RESTRINGING OF CONDUCTOR (R&B PH) BETWEEN LOC 208 TO 215 FOR CORRECTION OF SAG | 07/Jul/2026 | 08:00 | 07/Jul/2026 | 15:00 | RE DLV | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
58 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 07/Jul/2026 | 08:00 | 07/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
59 | OCC_239 | POWERGRID | 132KV-CHAPAKHOWA-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 07/Jul/2026 | 08:00 | 07/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-2, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
60 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 07/Jul/2026 | 7:00 | 07/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
61 | OCC_239 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation clearance | 07/Jul/2026 | 7:00 | 07/Jul/2026 | 16:00 | OK | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
62 | OCC_239 | POWERGRID | MISA - 400KV B/R 1 | D | AMP works and replacent of Aircell of Reactor | 07/Jul/2026 | 08:00 | 07/Jul/2026 | 20:00 |  | SD may be availed
63 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 07/Jul/2026 | 07:00 | 07/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
64 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 07/Jul/2026 | 07:00 | 07/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
65 | OCC_239 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation clearance | 08/Jul/2026 | 09:00 | 08/Jul/2026 | 15:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
66 | OCC_239 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | For maintenance works | 08/Jul/2026 | 09:00 | 08/Jul/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
67 | OCC_239 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | For maintenance works | 08/Jul/2026 | 09:00 | 08/Jul/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
68 | OCC_239 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 09/Jul/2026 | 09:00 | 09/Jul/2026 | 16:00 | RE GLG | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
69 | OCC_239 | POWERGRID | 400KV/220KV BONGAIGAON-ICT-2 | D | AMP works of ICT | 08/Jul/2026 | 7:00 | 08/Jul/2026 | 15:00 |  | SD may be availed subject to the availability of 400KV/220KV BONGAIGAON-ICT-1, 400/220kV ICTs at BgTPP and 220kV Alipurduar-Salakati D/C line
70 | OCC_239 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Routine Maintenance Work | 08/Jul/2026 | 09:00 | 08/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
71 | OCC_239 | TSECL | 132KV-AMBASA-MANU-1 | D | Routine Maintenance Work | 08/Jul/2026 | 09:00 | 08/Jul/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
72 | OCC_239 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | D | Jungle Cutting at Loc 280-287, 291-293 & 310-312 | 08/Jul/2026 | 08:00 | 08/Jul/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link. Intimation to Assam
73 | OCC_239 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | RESTRINGING OF CONDUCTOR (R&B PH) BETWEEN LOC 208 TO 215 FOR CORRECTION OF SAG | 08/Jul/2026 | 08:00 | 08/Jul/2026 | 15:00 | RE DLV | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
74 | OCC_239 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING, LOC 1 TO 65 | 08/Jul/2026 | 08:00 | 08/Jul/2026 | 16:00 | AGM MNI & AGM NGN | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
75 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 08/Jul/2026 | 08:00 | 08/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
76 | OCC_239 | POWERGRID | 132KV-HAFLONG-JIRIBAM-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM | 08/Jul/2026 | 7:00 | 08/Jul/2026 | 16:00 |  | SD may be availed subjected to availability of 132kV Khandong - Umrangsho - Haflong (PG)
77 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 08/Jul/2026 | 7:00 | 08/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
78 | OCC_239 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation clearance | 08/Jul/2026 | 7:00 | 08/Jul/2026 | 16:00 | OK | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
79 | OCC_239 | PENTL | 220KV/132KV NAMSAI-ICT-3 | D | AMP works of ICT | 11/Jul/2026 | 08:00 | 11/Jul/2026 | 17:00 |  | SD may be availed subject to the availability of 160MVA 220/132KV ICT-4 at Namsai, 220kV Kathalguri-Namsai D/C line and 132 kV Namsai - Tezu -Roing -Chapakhowa-Rupai link. Intimation to AP
80 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 08/Jul/2026 | 07:00 | 08/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
81 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 08/Jul/2026 | 07:00 | 08/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
82 | OCC_239 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING, LOC 1-35 | 09/Jul/2026 | 10:00 | 09/Jul/2026 | 16:00 | AGM TINSUKIA | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
83 | OCC_239 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation clearance | 09/Jul/2026 | 09:00 | 09/Jul/2026 | 15:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
84 | OCC_239 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 09/Jul/2026 | 09:00 | 09/Jul/2026 | 15:00 | AGM PANCHGRAM | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
85 | OCC_239 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Routine Maintenance Work | 09/Jul/2026 | 09:00 | 09/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
86 | OCC_239 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | RESTRINGING OF CONDUCTOR (R&B PH) BETWEEN LOC 208 TO 215 FOR CORRECTION OF SAG | 09/Jul/2026 | 08:00 | 09/Jul/2026 | 15:00 | RE DLV | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
87 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 09/Jul/2026 | 08:00 | 09/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
88 | OCC_239 | POWERGRID | 400KV/220KV MISA-ICT-2 | D | AMP WORKS & Replacement of Aircel. | 09/Jul/2026 | 7:00 | 09/Jul/2026 | 17:00 |  | SD may be availed subject to the availability of ICT 1 and ICT 3.
89 | OCC_239 | POWERGRID | 132KV-CHAPAKHOWA-ROING-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Jul/2026 | 08:00 | 09/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-1, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
90 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 09/Jul/2026 | 7:00 | 09/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
91 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 09/Jul/2026 | 07:00 | 09/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
92 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Installation of transmission line Surge Arrester | 09/Jul/2026 | 07:00 | 09/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
93 | OCC_239 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING, loc 314-238 | 09/Jul/2026 | 06:00 | 09/Jul/2026 | 15:00 | AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
94 | OCC_239 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | D | CORRIDOR CLEANING, loc 116-119 | 10/Jul/2026 | 10:00 | 10/Jul/2026 | 16:00 | RE MARGHERITA | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and kathalguri-Namsai-Tezu-Roing-Chapakhow-Rupai link
95 | OCC_239 | POWERGRID | 400 KV ALIPURDUAR 1 BAY (415) AT BONGAIGAON | D | AMP OF BAY EQUPMENTS | 10/Jul/2026 | 8:00 | 10/Jul/2026 | 16:00 |  | Sd may be availed subject to no outage of element. Intimation to NLDC
96 | OCC_239 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation clearance | 10/Jul/2026 | 09:00 | 10/Jul/2026 | 15:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
97 | OCC_239 | POWERGRID | 220KV/132KV DIMAPUR (PG)-ICT-3 | D | AMP & Relay testing works | 10/Jul/2026 | 09:00 | 10/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV ICT 1 and 2 at Dimapur
98 | OCC_239 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | AMP WORKS | 10/Jul/2026 | 09:00 | 10/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2.
99 | OCC_239 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Routine Maintenance Work | 10/Jul/2026 | 09:00 | 10/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. SD may be availed after restoration of 132kV PK Bari-Manu line. Intimation to Indigrid
100 | OCC_239 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | RESTRINGING OF CONDUCTOR (R&B PH) BETWEEN LOC 208 TO 215 FOR CORRECTION OF SAG | 10/Jul/2026 | 08:00 | 10/Jul/2026 | 15:00 | RE DLV | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
101 | OCC_239 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING, LOC 66 TO 95 | 10/Jul/2026 | 08:00 | 10/Jul/2026 | 16:00 | AGM MNI & AGM NGN | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
102 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 10/Jul/2026 | 08:00 | 10/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
103 | OCC_239 | POWERGRID | 132KV/33KV IMPHAL(PG)-ICT-1 | D | AMP works of ICT | 10/Jul/2026 | 08:00 | 10/Jul/2026 | 15:00 |  | SD may be availed subject to the availability of ICT2. Consent from Manipur
104 | OCC_239 | POWERGRID | 132KV-CHAPAKHOWA-ROING-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Jul/2026 | 08:00 | 10/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-1, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
105 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 10/Jul/2026 | 7:00 | 10/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
106 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 10/Jul/2026 | 07:00 | 10/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
107 | OCC_239 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | D | Monthly chnageover of 3*105MVA transformer (R,B&Spare phases ICT will be charged) | 11/Jul/2026 | 11:00 | 11/Jul/2026 | 13:00 | no load will be affected during the shutdown | SD may be availed subject to availability of 132kV Imphal – Yingagangpokpi-Kongba-New Thoubal – Old Thoubal – Kakching – Churachandpur – Ningthoukhong link. Manipur demand to be kept below 170 MW to avoid low voltage under n-1 contingecy of 132kV Ningthoukhong – Churachandpur II.
108 | OCC_239 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 11/Jul/2026 | 09:00 | 11/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link
109 | OCC_239 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | RESTRINGING OF CONDUCTOR (R&B PH) BETWEEN LOC 208 TO 215 FOR CORRECTION OF SAG | 11/Jul/2026 | 08:00 | 11/Jul/2026 | 15:00 | RE DLV | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
110 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 11/Jul/2026 | 08:00 | 11/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
111 | OCC_239 | POWERGRID | 132KV-BADARPUR-KHLIEHRIAT-1 | D | Replacment of insulator due to flashover dated 20.03.2026 at Loc- 49-50 by Silchar TLM. | 11/Jul/2026 | 7:00 | 11/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Badarpur – Panchgram – Lunshnong-Khliehriat link, 132kV Khandong – Khleihriat link,132kV Khleihriat(PG)-Khleihriat(ME) D/C and 220kV Killing – Mawngap D/C
112 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 11/Jul/2026 | 7:00 | 11/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
113 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 11/Jul/2026 | 07:00 | 11/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
114 | OCC_239 | AEGCL | NALKATA - 132KV - BUS 1 | D | (MAIN BUS) AUGMENTATION WORK | 11/Jul/2026 | 03:30 | 11/Jul/2026 | 07:00 | MAIN BUS, AGM NLK | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, NEEPCO and MUML
115 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Routine Maintenance Work | 12/Jul/2026 | 09:00 | 12/Jul/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
116 | OCC_239 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Routine Maintenance Work | 12/Jul/2026 | 09:00 | 12/Jul/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
117 | OCC_239 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Routine Maintenance Work | 12/Jul/2026 | 09:00 | 12/Jul/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
118 | OCC_239 | TSECL | 132KV-BODHJUNGNAGAR-JIRANIA-1 | D | Routine Maintenance Work | 12/Jul/2026 | 09:00 | 12/Jul/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
119 | OCC_239 | TSECL | BUDHJANGNAGAR - 132KV - BUS 1 | D | Routine Maintenance Work | 12/Jul/2026 | 09:00 | 12/Jul/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
120 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 12/Jul/2026 | 08:00 | 12/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
121 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 12/Jul/2026 | 07:00 | 12/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
122 | OCC_239 | AEGCL | NALKATA - 132KV - BUS 1 | D | (MAIN BUS) AUGMENTATION WORK | 12/Jul/2026 | 03:30 | 12/Jul/2026 | 07:00 | MAIN BUS, AGM NLK | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
123 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 13/Jul/2026 | 08:00 | 13/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
124 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 13/Jul/2026 | 7:00 | 13/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
125 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 13/Jul/2026 | 07:00 | 13/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
126 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 13/Jul/2026 | 07:00 | 13/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
127 | OCC_239 | AEGCL | NALKATA - 132KV - BUS 1 | D | (MAIN BUS) AUGMENTATION WORK | 13/Jul/2026 | 03:30 | 13/Jul/2026 | 07:00 | MAIN BUS, AGM NLK | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
128 | OCC_239 | POWERGRID | 400 KV, 125 MVAR BUS REACTOR 5 BAY AT BONGAIGAON | D | AMP OF BAY EQUPMENTS | 14/Jul/2026 | 8:00 | 14/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of tie bay of 125 MVAR Bus Reactor V and 315 MVA ICT II@Bongaigaon and main bay of 315 MVA ICT II@Bongaigaon
129 | OCC_239 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations at 152,269,251,125,263,76 by Dimapur TLM | 14/Jul/2026 | 09:00 | 14/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-II ckt & 132kV Doyang - Mokokchung(NL). Intimation to NEEPCO
130 | OCC_239 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 14/Jul/2026 | 09:00 | 14/Jul/2026 | 16:00 | Shutdown not required. Only A/R Non Auto for Circuit-2 while working on Circuit-1 | A/R may be kept in Non-Auto mode
131 | OCC_239 | POWERGRID | TIE BAY () OF 400KV-SILCHAR-IMPHAL(PG)-2 AND 400KV/132KV IMPHAL(PG)-ICT-2 @IMPHAL(PG) - 400KV | D | AMP of bay equipmentAMP of bay equipment | 14/Jul/2026 | 09:00 | 14/Jul/2026 | 14:00 |  | S/D may be availed subject to availability of 400kV Silchar-Imphal 2 main bay and 400/132kV ICT-2 main bay at 400kV Imphal(PG)
132 | OCC_239 | POWERGRID | MISA - 400KV B/R 2 | D | AMP WORKS & Replacement of PRD Limit Switch | 14/Jul/2026 | 09:00 | 14/Jul/2026 | 18:00 |  | SD may be availed
133 | OCC_239 | TSECL | 132KV-AMBASA-MANU-1 | D | Routine Maintenance Work | 14/Jul/2026 | 09:00 | 14/Jul/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
134 | OCC_239 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 15/Jul/2026 | 08:00 | 15/Jul/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
135 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 14/Jul/2026 | 08:00 | 14/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line.
136 | OCC_239 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | CB Close coil timing mismatch problem checking, testing. AMP of bay equipment. | 14/Jul/2026 | 08:00 | 14/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period.Consent from Assam
137 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 14/Jul/2026 | 7:00 | 14/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
138 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 14/Jul/2026 | 07:00 | 14/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
139 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 14/Jul/2026 | 07:00 | 14/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
140 | OCC_239 | AEGCL | NALKATA - 132KV - BUS 1 | D | (MAIN BUS) AUGMENTATION WORK | 14/Jul/2026 | 03:30 | 14/Jul/2026 | 07:00 | MAIN BUS, AGM NLK | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
141 | OCC_239 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 15/Jul/2026 | 09:00 | 15/Jul/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service. Intimation to NERTS
142 | OCC_239 | POWERGRID | 132KV-KHANDONG-KOPILI -2 | D | AMP of bay equipemnts at KhandongSS by Umranshu TLM | 15/Jul/2026 | 8:00 | 15/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV KHANDONG(NEEPCO)-KOPILI(NEEPCO)-1 line,132kV Khandong - Khleriat DC and 132kV Khandong - Umrangsu-Haflong(PG)-Jiribam line. Intimation to NEEPCO
143 | OCC_239 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations at 152,269,251,125,263,76 by Dimapur TLM | 15/Jul/2026 | 09:00 | 15/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-II ckt & 132kV Doyang - Mokokchung(NL). Intimation to NEEPCO
144 | OCC_239 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 15/Jul/2026 | 09:00 | 15/Jul/2026 | 16:00 | Shutdown not required. Only A/R Non Auto for Circuit-2 while working on Circuit-1 | A/R may be kept in Non-Auto mode
145 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 15/Jul/2026 | 08:00 | 15/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
146 | OCC_239 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | C | Stringing of DIVERSION LOC 130 & 133 of 132 KV JIRIBAM-LOKTAK TL | 15/Jul/2026 | 08:00 | 21/Jul/2026 | 17:30 |  | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line. SPS at Loktak related to tripping of one unit in case of outage two lines evacuation from Loktak(excl. 132kV Loktak - Rengpang) to be kept in ON condition during the shutdown period. Consent from NHPC is required
147 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 15/Jul/2026 | 7:00 | 15/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
148 | OCC_239 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Shutdown was deffered in the month of May 2026 due to system constraints. | 15/Jul/2026 | 08:00 | 15/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
149 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 15/Jul/2026 | 07:00 | 15/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
150 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 15/Jul/2026 | 07:00 | 15/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
151 | OCC_239 | AEGCL | NALKATA - 132KV - BUS 1 | D | (MAIN BUS) AUGMENTATION WORK | 15/Jul/2026 | 03:30 | 15/Jul/2026 | 07:00 | MAIN BUS, AGM NLK | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
152 | OCC_239 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 16/Jul/2026 | 09:00 | 16/Jul/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
153 | OCC_239 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations at 33,64,125,133 & 231 by Dimapur TLM | 16/Jul/2026 | 09:00 | 16/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-I & 132kV Doyang - Mokokchung(NL). Intimation to NEEPCO
154 | OCC_239 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | D | PREVENTIVE MAINTENANCE, JUMPER CHECKING, LOC 1 TO 75 | 16/Jul/2026 | 08:00 | 16/Jul/2026 | 15:00 | AGM NAGAON T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
155 | OCC_239 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 16/Jul/2026 | 08:00 | 16/Jul/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
156 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 16/Jul/2026 | 08:00 | 16/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
157 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 16/Jul/2026 | 7:00 | 16/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
158 | OCC_239 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Shutdown was deffered in the month of May 2026 due to system constraints. | 16/Jul/2026 | 08:00 | 16/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
159 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 16/Jul/2026 | 07:00 | 16/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
160 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 16/Jul/2026 | 07:00 | 16/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
161 | OCC_239 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEANING, LOC 84-134 | 17/Jul/2026 | 10:00 | 17/Jul/2026 | 16:00 | AGM TINSUKIA | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
162 | OCC_239 | POWERGRID | MAIN BAY () OF 400KV/220KV BONGAIGAON-ICT-1 @BONGAIGAON - 400KV | D | AMP OF BAY EQUPMENTS | 17/Jul/2026 | 8:00 | 17/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of tie bay of 400/220kV 315 MVA ICT I & 400kV New Siliguri I@400kV Bongaigaon(PG) and main bay of 400kV New Siliguri I@400kV Bongaigaon(PG). Intimation to NLDC
163 | OCC_239 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 17/Jul/2026 | 09:00 | 17/Jul/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
164 | OCC_239 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 17/Jul/2026 | 09:00 | 17/Jul/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
165 | OCC_239 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations at 33,64,125,133 & 231 by Dimapur TLM | 17/Jul/2026 | 09:00 | 17/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 1320kV Doyang-Diampur-I & 132kV Doyang - Mokokchung(NL). Intimation to NEEPCO
166 | OCC_239 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Routine Maintenance Work | 17/Jul/2026 | 09:00 | 17/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
167 | OCC_239 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | D | PREVENTIVE MAINTENANCE, JUMPER CHECKING, LOC 90 TO 143 | 17/Jul/2026 | 08:00 | 17/Jul/2026 | 15:00 | AGM NAGAON T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
168 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 17/Jul/2026 | 08:00 | 17/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
169 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 17/Jul/2026 | 7:00 | 17/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
170 | OCC_239 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Shutdown was deffered in the month of May 2026 due to system constraints. | 17/Jul/2026 | 08:00 | 17/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link
171 | OCC_239 | POWERGRID | MARIANI (PG) - 220KV B/R 1 | D | AMP works | 17/Jul/2026 | 08:00 | 17/Jul/2026 | 16:00 |  | SD may be availed
172 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 17/Jul/2026 | 07:00 | 17/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
173 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 17/Jul/2026 | 07:00 | 17/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
174 | OCC_239 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING, loc 97-102 | 18/Jul/2026 | 10:00 | 18/Jul/2026 | 16:00 | RE MARGHERITA | S/D may be availed subject to the availability of 132kV Tinsukia-Rupai and 132kV Tinsukia-Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
175 | OCC_239 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | CORRIDOR CLEANING | 18/Jul/2026 | 09:00 | 18/Jul/2026 | 16:00 | AGM T& T GOALPARA | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
176 | OCC_239 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING | 18/Jul/2026 | 7:00 | 18/Jul/2026 | 14:00 | AGM T& T GOALPARA | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 380 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high
177 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 18/Jul/2026 | 08:00 | 18/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line.
178 | OCC_239 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations | 18/Jul/2026 | 7:00 | 18/Jul/2026 | 16:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
179 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 18/Jul/2026 | 07:00 | 18/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
180 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 18/Jul/2026 | 07:00 | 18/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
181 | OCC_239 | POWERGRID | BUS COUPLER BAY () OF JIRIBAM(PG) - 132KV - BUS 1 AND JIRIBAM(PG) - 132KV - BUS 2 @JIRIBAM(PG) - 132KV | D | Warranty testing of GIS bay at Jiribam SS | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 16:00 |  | SD may be availed. Proper segragation of Elements to be done before availing the SD
182 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 19/Jul/2026 | 08:00 | 19/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
183 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 19/Jul/2026 | 07:00 | 19/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
184 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 19/Jul/2026 | 07:00 | 19/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
185 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 20/Jul/2026 | 08:00 | 20/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
186 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 20/Jul/2026 | 07:00 | 20/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
187 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Installation of transmission line Surge Arrester | 20/Jul/2026 | 07:00 | 20/Jul/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
188 | OCC_239 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 21/Jul/2026 | 09:00 | 21/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
189 | OCC_239 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 21/Jul/2026 | 08:00 | 21/Jul/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
190 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 21/Jul/2026 | 08:00 | 21/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
191 | OCC_239 | POWERGRID | 132KV-BADARPUR-KARIMGANJ (AS)-1 | D | Replacment of insulator due to flashover dated 17.03.2026 at Loc- 60 by Silchar TLM. | 21/Jul/2026 | 7:00 | 21/Jul/2026 | 16:00 |  | Shutdown may be availed subject to availability of 132kV Kumarghat - Karimganj. Consent from Assam
192 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 21/Jul/2026 | 07:00 | 21/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
193 | OCC_239 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 237-162 | 21/Jul/2026 | 06:00 | 21/Jul/2026 | 15:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
194 | OCC_239 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING, LOC 1-54 | 22/Jul/2026 | 10:00 | 22/Jul/2026 | 16:00 | AGM TINSUKIA | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
195 | OCC_239 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 22/Jul/2026 | 09:00 | 22/Jul/2026 | 16:00 | AGM T& T GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
196 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 22/Jul/2026 | 08:00 | 22/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
197 | OCC_239 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | Repairing of damaged TLSA due to lightning at loc. 402,279,286,296,313 by Aizwal TLM | 22/Jul/2026 | 7:00 | 22/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
198 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 22/Jul/2026 | 07:00 | 22/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode. SD deferred due to SD of 132KV-AIZWAL-TIPAIMUMK-1
199 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 22/Jul/2026 | 07:00 | 22/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
200 | OCC_239 | AEGCL | 220KV-AGIA-AZARA-1 | D | CORRIDOR CLEANING | 23/Jul/2026 | 09:00 | 23/Jul/2026 | 16:00 | AGM T& T GOALPARA | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
201 | OCC_239 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 23/Jul/2026 | 09:00 | 23/Jul/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
202 | OCC_239 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 23/Jul/2026 | 08:00 | 23/Jul/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
203 | OCC_239 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | SHIFTING OF 132kV AIS BAY TO GIS BAY | 23/Jul/2026 | 08:00 | 23/Jul/2026 | 15:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
204 | OCC_239 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | Repairing of damaged TLSA due to lightning at loc. 402,279,286,296,313 by Aizwal TLM | 23/Jul/2026 | 7:00 | 23/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
205 | OCC_239 | POWERGRID | MARIANI (PG) - 400KV - BUS 1 | D | AMP and Busbar testing Works | 23/Jul/2026 | 08:00 | 23/Jul/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
206 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 23/Jul/2026 | 07:00 | 23/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode. SD deferred due to SD of 132KV-AIZWAL-TIPAIMUMK-1
207 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 23/Jul/2026 | 07:00 | 23/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
208 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 55, 59, 101, 112, | 24/Jul/2026 | 09:00 | 24/Jul/2026 | 17:00 |  | SD deferred
209 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 24/Jul/2026 | 09:00 | 24/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-2 while working in Circuit-1 | SD deferred
210 | OCC_239 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Routine Maintenance Work | 24/Jul/2026 | 09:00 | 24/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
211 | OCC_239 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | Repairing of damaged TLSA due to lightning at loc. 402,279,286,296,313 by Aizwal TLM | 24/Jul/2026 | 7:00 | 24/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
212 | OCC_239 | POWERGRID | MARIANI (PG) - 400KV - BUS 2 | D | AMP and Busbar testing Works | 24/Jul/2026 | 08:00 | 24/Jul/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
213 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 24/Jul/2026 | 07:00 | 24/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode. SD deferred due to SD of 132KV-AIZWAL-TIPAIMUMK-1
214 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 24/Jul/2026 | 07:00 | 24/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
215 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 55, 59, 101, 112, | 25/Jul/2026 | 09:00 | 25/Jul/2026 | 17:00 |  | SD deferred
216 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 25/Jul/2026 | 09:00 | 25/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-2 while working in Circuit-1 | SD deferred
217 | OCC_239 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Routine Maintenance Work | 25/Jul/2026 | 09:00 | 25/Jul/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
218 | OCC_239 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | Repairing of damaged TLSA due to lightning at loc. 402,279,286,296,313 by Aizwal TLM | 25/Jul/2026 | 7:00 | 25/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
219 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 25/Jul/2026 | 07:00 | 25/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode. SD deferred due to SD of 132KV-AIZWAL-TIPAIMUMK-1
220 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 25/Jul/2026 | 07:00 | 25/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
221 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 55, 59, 101, 112, | 26/Jul/2026 | 09:00 | 26/Jul/2026 | 17:00 |  | SD deferred
222 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 26/Jul/2026 | 09:00 | 26/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-2 while working in Circuit-1 | SD deferred
223 | OCC_239 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 26/Jul/2026 | 09:00 | 26/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
224 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 26/Jul/2026 | 09:00 | 26/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
225 | OCC_239 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Routine Maintenance Work | 26/Jul/2026 | 09:00 | 26/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
226 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 26/Jul/2026 | 07:00 | 26/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
227 | OCC_239 | POWERGRID | 132KV-BADARPUR-PANCHGRAM (NEW)-1 | D | AMP of Bay and line equipments at Badarpur SS | 27/Jul/2026 | 8:00 | 27/Jul/2026 | 16:00 |  | S/D may be availed subject to the availabilty of 132kV Panchgram-Lumnsnong -Khleihriat line.
228 | OCC_239 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | C | Circuit Breaker Mechanism Replacement | 27/Jul/2026 | 09:00 | 28/Jul/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Consent from Nagaland is required
229 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 55, 59, 101, 112, | 27/Jul/2026 | 09:00 | 27/Jul/2026 | 17:00 |  | SD deferred
230 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | Shutdown of Circuit-2 not required. AR in Non-auto mode of circuit-2 for replacement of insulator for circuit-1. | 27/Jul/2026 | 09:00 | 27/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-2 while working in Circuit-1 | SD deferred
231 | OCC_239 | NTPC | 400KV-BGTPP-BONGAIGAON-2 | C | Line 2 CVT TESTING & CONDUCTOR CHECKING | 27/Jul/2026 | 09:00 | 27/Jul/2026 | 18:00 |  | SD deferred
232 | OCC_239 | NTPC | 400 KV BONGAIGAON 1 BAY (401) AT BGTPP | C | 400KV BAY 1 CVT CONDUCTOR CHECKING | 27/Jul/2026 | 09:00 | 27/Jul/2026 | 18:00 |  | SD deferred
233 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 27/Jul/2026 | 08:00 | 27/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
234 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 27/Jul/2026 | 07:00 | 27/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
235 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 27/Jul/2026 | 07:00 | 27/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
236 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 60, 64, 101, 116, 166 | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 17:00 |  | SD deferred
237 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-1 while working in Circuit-02 | SD deferred
238 | OCC_239 | NTPC | 400KV-BGTPP-BONGAIGAON-1 | C | Line 1 CVT TESTING & CONDUCTOR CHECKING | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 18:00 |  | SD deferred
239 | OCC_239 | NTPC | 400 KV BONGAIGAON 2 BAY (402) AT BGTPP | C | 400KV BAY 2 CVT CONDUCTOR CHECKING | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 18:00 |  | SD deferred
240 | OCC_239 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Routine Maintenance Work | 28/Jul/2026 | 09:00 | 28/Jul/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
241 | OCC_239 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 28/Jul/2026 | 08:00 | 28/Jul/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
242 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 28/Jul/2026 | 08:00 | 28/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
243 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 28/Jul/2026 | 07:00 | 28/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
244 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 28/Jul/2026 | 07:00 | 28/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
245 | OCC_239 | NETCL | 400KV-BONGAIGAON-BYRNIHAT (KILLING) | D | Replacement of damaged insulators, tightening of loose jumper cone N&B etc. | 19/Jul/2026 | 10:00 | 19/Jul/2026 | 16:00 | Put up for approval in the 239th OCCM. | S/D may be availed subject to availability of 400 kV Bongaigaon – Azara, 400 kV Silchar – Killing, 400 kV Silchar – Azara, 220 kV Agia – BTPS D/C, 220 kV Balipara – Sonabil – Samaguri D/C. The combined loading of the 220 kV BTPS–Agia D/C line should be maintained below 240 MW during the shutdown period to ensure safe and reliable operation. ATC/TTC needs to be revised. SD may be deferred on high demand period
246 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 60, 64, 101, 116, 166 | 29/Jul/2026 | 09:00 | 29/Jul/2026 | 17:00 |  | SD deferred
247 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 29/Jul/2026 | 09:00 | 29/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-1 while working in Circuit-02 | SD deferred
248 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 29/Jul/2026 | 08:00 | 29/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
249 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 29/Jul/2026 | 07:00 | 29/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
250 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 29/Jul/2026 | 07:00 | 29/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
251 | OCC_239 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING, loc 237-162 | 29/Jul/2026 | 06:00 | 29/Jul/2026 | 15:00 | AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
252 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 60, 64, 101, 116, 166 | 30/Jul/2026 | 09:00 | 30/Jul/2026 | 17:00 |  | SD deferred
253 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 30/Jul/2026 | 09:00 | 30/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-1 while working in Circuit-02 | SD deferred
254 | OCC_239 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 30/Jul/2026 | 08:00 | 30/Jul/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
255 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 30/Jul/2026 | 08:00 | 30/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
256 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 30/Jul/2026 | 07:00 | 30/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
257 | OCC_239 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 30/Jul/2026 | 07:00 | 30/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
258 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations 60, 64, 101, 116, 166 | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 17:00 |  | SD deferred
259 | OCC_239 | POWERGRID | A/R of 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 17:00 | Shutdown not required. Only AR Non-Auto required for circuit-1 while working in Circuit-02 | SD deferred
260 | OCC_239 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Routine Maintenance Work | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
261 | OCC_239 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
262 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | Shutdown of Circuit-1 not required. AR in Non-auto mode of circuit-1 for replacement of insulator for circuit-2. | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 17:00 |  | SD deferred
263 | OCC_239 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing | 31/Jul/2026 | 09:00 | 31/Jul/2026 | 17:00 |  | SD deferred
264 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 31/Jul/2026 | 08:00 | 31/Jul/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
265 | OCC_239 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. | 31/Jul/2026 | 08:00 | 31/Jul/2026 | 16:00 |  | SD deferred
266 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 31/Jul/2026 | 07:00 | 31/Jul/2026 | 16:00 | Shutdown not required. AR in Non-Auto in required. | A/R may be kept in Non-Auto mode
267 | OCC_239 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non - Auto mode required for OPGW insstallation works under Reliable Communication Scheme. | 31/Jul/2026 | 07:00 | 31/Jul/2026 | 16:00 |  | SD deferred