## Sheet1
Sl no. | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Study Comments | SD Status
1 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Routine Maintenance Work | 01/Aug/2026 | 09:00 | 01/Aug/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
2 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 01/Aug/2026 | 08:00 | 01/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
3 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 01/Aug/2026 | 07:00 | 01/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
4 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 02/Aug/2026 | 08:00 | 02/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
5 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 02/Aug/2026 | 07:00 | 02/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
6 | OCC_240 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Aug/2026 | 10:00 | 03/Aug/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
7 | OCC_240 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 03/Aug/2026 | 8:00 | 03/Aug/2026 | 15:00 | AGM T&T GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
8 | OCC_240 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Jungle Clerance | 03/Aug/2026 | 8:00 | 03/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
9 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Routine Maintenance Work | 03/Aug/2026 | 09:00 | 03/Aug/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
10 | OCC_240 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement in Loc. 23,24,26,68,69 | 03/Aug/2026 | 09:00 | 03/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred
11 | OCC_240 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING 74 TO 35 | 03/Aug/2026 | 08:30 | 03/Aug/2026 | 16:30 | AGM SSJI | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
12 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 03/Aug/2026 | 08:00 | 03/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
13 | OCC_240 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 334-442 | 03/Aug/2026 | 08:00 | 03/Aug/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
14 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 03/Aug/2026 | 07:00 | 03/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
15 | OCC_240 | NEEPCO | AGBPP - STG 2 | C | Major Inspection/ Major Overhauling of Generator & Exciter | 03/Aug/2026 | 00:00 | 30/Aug/2026 | 23:59 |  | SD may be availed. Consent from Beneficiaries
16 | OCC_240 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Jiribam TLM , Loc No- 107,108, 233,234,240,241, | 04/Aug/2026 | 08:00 | 04/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh. Consent from to Manipur
17 | OCC_240 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 28/Aug/2026 | 10:00 | 28/Aug/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, and 220kV Mawngap - Killing D/C shall be kept in service. Consent from Meghalaya.
18 | OCC_240 | MEPTCL | 132KV-KHLIEHRIAT(ME)-KHELIEHRIAT-2 | D | Thorough checking of lines especially of nuts and bolts, checking of disc insulator and jumper clamps, where climbing of towers will be required (Loc. 1 to Loc. 204) | 04/Aug/2026 | 10:00 | 04/Aug/2026 | 16:00 | Avail | SD may be availed subject to availability of 132kV Khleihriat - Khleihriat II, 132kV Badarpur - Panchgram - Lumshnong- Khliehriat link and 220kV Killing - Mawngap D/C. Intimation to NERTS
19 | OCC_240 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING LOC 85 TO 130 | 09/Aug/2026 | 7:00 | 09/Aug/2026 | 14:00 | AGM T&T GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high
20 | OCC_240 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Jungle Clerance | 04/Aug/2026 | 8:00 | 04/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
21 | OCC_240 | POWERGRID | 220KV-BONGAIGAON-SALAKATI-1 | D | AMP of Bay Equipments | 04/Aug/2026 | 8:00 | 04/Aug/2026 | 15:30 |  | SD may be availed subject to the availability of 220KV-BONGAIGAON-SALAKATI-2, 220kV Bongaigaon-BTPS D/C(ICT)
22 | OCC_240 | POWERGRID | 132KV-BISWANATH CHARIALI-PAVOI-2 | D | Relay Testing Work at Pavoi end | 01/Aug/2026 | 8:00 | 01/Aug/2026 | 16:00 |  | SD may be availed subjected to availability of 132kV BNC - Pavoi 1, 132kV BNC - Gohpur and 132kV Pavoi - Gohpur D/C. Consent from Assam
23 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. Shutdown not required | 04/Aug/2026 | 09:00 | 04/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
24 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. | 04/Aug/2026 | 09:00 | 04/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
25 | OCC_240 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement in Loc. 23,24,26,68,69 | 04/Aug/2026 | 09:00 | 04/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred
26 | OCC_240 | POWERGRID | MAIN BAY () OF 400KV-BISWANATH CHARIALI-BALIPARA-2 @BALIPARA - 400KV | C | For Y phase CB pole overhauling to rectify SF6 gas leakage | 04/Aug/2026 | 09:00 | 07/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of Tie bay of 400kV Balipara-Misa II & 400kV Balipara-Biswanath Chariali II at 400kV Balipara and Main bay of 400kV Balipara-Misa II at 400kV Balipara
27 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 04/Aug/2026 | 08:00 | 04/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
28 | OCC_240 | AEGCL | 132KV-GOHPUR-PAVOI-2 | C | SHIFTING 132kV AIS BAY TO GIS BAY | 04/Aug/2026 | 08:00 | 23/Aug/2026 | 18:00 | RE GOHPUR | S/D may be availed
29 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 04/Aug/2026 | 07:00 | 04/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
30 | OCC_240 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 314 TO 238 | 04/Aug/2026 | 07:00 | 04/Aug/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
31 | OCC_240 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING LOC 1 TO 42 | 05/Aug/2026 | 9:00 | 05/Aug/2026 | 16:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
32 | OCC_240 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Jiribam TLM , Loc No- 107,108, 233,234,240,241, | 05/Aug/2026 | 8:00 | 05/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh. Consent from to Manipur
33 | OCC_240 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 105 to 103. | 05/Aug/2026 | 10:00 | 05/Aug/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
34 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Routine Maintenance Work | 05/Aug/2026 | 09:00 | 05/Aug/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
35 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. Shutdown not required | 05/Aug/2026 | 09:00 | 05/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
36 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. | 05/Aug/2026 | 09:00 | 05/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
37 | OCC_240 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement in Loc. 23,24,26,68,69 | 05/Aug/2026 | 09:00 | 05/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred
38 | OCC_240 | POWERGRID | TIE BAY () OF 400KV-IMPHAL(PG)-400 KV NEW KOHIMA-1 AND 400KV/132KV IMPHAL(PG)-ICT-1 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 05/Aug/2026 | 09:00 | 05/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of main bay of 400kV Imphal-New Kohima-1 at Imphal-400kV & main bay of 315 MVA ICT 1 at Imphal-400kV
39 | OCC_240 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 209 TO 215 | 05/Aug/2026 | 7:00 | 05/Aug/2026 | 15:00 | AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
40 | OCC_240 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | D | Maintenance Work | 05/Aug/2026 | 08:00 | 05/Aug/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
41 | OCC_240 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | D | Maintenance Work | 05/Aug/2026 | 08:00 | 05/Aug/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
42 | OCC_240 | PENTL | 220KV/132KV NAMSAI-ICT-4 | D | AMP of ICT | 05/Aug/2026 | 7:00 | 05/Aug/2026 | 16:00 | Sample Remarks | SD may be availed subject to the availability of 160MVA 220/132KV ICT-3 at Namsai, 220kV Kathalguri-Namsai D/C line, 132kV Panyor-Ziro-Daporizo-Basar-Along-Pasighat-Roing link and 132 kV Namsai - Tezu -Roing -Chapakhowa-Rupai link.
43 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 05/Aug/2026 | 08:00 | 05/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
44 | OCC_240 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 334-442 | 05/Aug/2026 | 08:00 | 05/Aug/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
45 | OCC_240 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 101-149 | 05/Aug/2026 | 08:00 | 05/Aug/2026 | 15:00 | AGM NLK | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
46 | OCC_240 | AEGCL | 400KV-AZARA-SILCHAR | D | ROUTINE BAY MAINTENANCE | 05/Aug/2026 | 07:00 | 05/Aug/2026 | 16:00 | AGM MIRZA | S/D may be availed subject to the availability of 400kV Bongaigaon-Azara, 220kV Agia BTPS D/C, Salakati-BTPS D/C and 400kV Bongaiagon-Killing-Silchar link
47 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 05/Aug/2026 | 07:00 | 05/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
48 | OCC_240 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Jiribam TLM , Loc No- 107,108, 233,234,240,241, | 06/Aug/2026 | 8:00 | 06/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh. Consent from to Manipur
49 | OCC_240 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Aug/2026 | 10:00 | 06/Aug/2026 | 16:00 | AGM PNG | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
50 | OCC_240 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING LOC 85 TO 130 | 16/Aug/2026 | 7:00 | 16/Aug/2026 | 14:00 | AGM T&T GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
51 | OCC_240 | POWERGRID | 400KV-BALIPARA-MISA-1 | D | Rectification of Conductor strands 2 nos damaged in Bottom Phase of Span Location loc 198-199 CKt-1 and to carry out other Shutdown defect rectification such as VD slippage. | 06/Aug/2026 | 7:00 | 06/Aug/2026 | 14:00 |  | SD may be availed subject to the availability of 400kV Balipara - Misa-2 and 220kV Balaipara - Sonabil D/C. SPS related to overloading of 220kV Balipara - Sonabil D/C is to be kept in ON condition during the shutdown period. The SD will be deferred when the NER demand is high
52 | OCC_240 | POWERGRID | A/R of 400KV-BALIPARA-MISA-2 | D | Line will be in service, only AR in Non-Auto mode | 06/Aug/2026 | 7:00 | 06/Aug/2026 | 14:00 |  | A/R may be kept in Non-Auto mode
53 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. Shutdown not required | 06/Aug/2026 | 09:00 | 06/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
54 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. | 06/Aug/2026 | 09:00 | 06/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
55 | OCC_240 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement in Loc. 82.102.124,126,127,129 | 06/Aug/2026 | 8:00 | 06/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Intimation to Assam
56 | OCC_240 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 1 TO 159 | 06/Aug/2026 | 09:00 | 06/Aug/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Daporizo-Basar-Along-Pasighat-Roing link. Intimation to AP and NERTS
57 | OCC_240 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 06/Aug/2026 | 09:00 | 06/Aug/2026 | 16:00 | RE GLG | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
58 | OCC_240 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 06/Aug/2026 | 09:00 | 06/Aug/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
59 | OCC_240 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | D | Warranty Test 1. SF6 Gas Quality Checks 2. CB Operation Checks (Timing, CRM, DCRM, etc) 3. GD monitor Alarm/Trip Test along with signal validation with RTAMC 4. Checking of interlocks 5. CRM test for all circuits 6. IR test of SF6 to Air Bushing 7. LA IR Test | 06/Aug/2026 | 8:00 | 06/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
60 | OCC_240 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 74 TO 42 | 06/Aug/2026 | 08:30 | 06/Aug/2026 | 16:30 | AGM SSJI & agm smg | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
61 | OCC_240 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | D | Maintenance Work | 06/Aug/2026 | 08:00 | 06/Aug/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
62 | OCC_240 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | D | Maintenance Work | 06/Aug/2026 | 08:00 | 06/Aug/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
63 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 06/Aug/2026 | 08:00 | 06/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
64 | OCC_240 | POWERGRID | MARIANI (PG) - 400KV B/R 2 | D | Warranty test of 400KV Bus Reactor-2(412R) 1.Bushing Tan delta & capacitance test 2.Winding Tan delta & capacitance test 3.Core Insulation test 4.Mechanical protection checking 5.Cable IR etc. | 06/Aug/2026 | 08:00 | 06/Aug/2026 | 16:00 |  | SD may be availed
65 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 06/Aug/2026 | 07:00 | 06/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
66 | OCC_240 | POWERGRID | 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Jiribam TLM , Loc No- 107,108, 233,234,240,241, | 07/Aug/2026 | 8:00 | 07/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Aizawl-Tipaimukh. Consent from to Manipur
67 | OCC_240 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Aug/2026 | 10:00 | 07/Aug/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
68 | OCC_240 | AEGCL | 220KV-AGIA-AZARA-1 ( 132kV Agia-Chaygaon line) | D | CORRIDOR CLEANING | 08/Aug/2026 | 8:00 | 08/Aug/2026 | 15:00 | AGM T&T GOALPARA | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
69 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. Shutdown not required | 07/Aug/2026 | 09:00 | 07/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
70 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. | 07/Aug/2026 | 09:00 | 07/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
71 | OCC_240 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement in Loc. 82.102.124,126,127,129 | 07/Aug/2026 | 8:00 | 07/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Consent from Assam
72 | OCC_240 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Aug/2026 | 09:00 | 07/Aug/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service. Intimation to NERTS
73 | OCC_240 | POWERGRID | MAIN BAY () OF 400KV-IMPHAL(PG)-400 KV NEW KOHIMA-1 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 07/Aug/2026 | 09:00 | 07/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of Tie bay of 400kV Imphal-New Kohima-1 & main bay of 315 MVA ICT 1 at Imphal-400kV and main bay of 315 MVA ICT 1 at Imphal-400kV
74 | OCC_240 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | D | Warranty Test 1. SF6 Gas Quality Checks 2. CB Operation Checks (Timing, CRM, DCRM, etc) 3. GD monitor Alarm/Trip Test along with signal validation with RTAMC 4. Checking of interlocks 5. CRM test for all circuits 6. IR test of SF6 to Air Bushing 7. LA IR Test | 07/Aug/2026 | 8:00 | 07/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
75 | OCC_240 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 229 TO 261 | 07/Aug/2026 | 7:00 | 07/Aug/2026 | 15:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
76 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 07/Aug/2026 | 08:00 | 07/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
77 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Installation of transmission line Surge Arrester | 07/Aug/2026 | 07:00 | 07/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
78 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Routine Maintenance Work | 08/Aug/2026 | 09:00 | 08/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV SM Nagar-Bodhjunagar-SM Nagar(TE) link
79 | OCC_240 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 08/Aug/2026 | 09:00 | 08/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
80 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-1 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. Shutdown not required | 08/Aug/2026 | 09:00 | 08/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
81 | OCC_240 | POWERGRID | A/R of 400KV-SILCHAR-IMPHAL(PG)-2 | D | AR in NON - AUTO MODE required for Sample PID scanning works of Porcelain disc insulators at various towers under Imphal jurisdiction. | 08/Aug/2026 | 09:00 | 08/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
82 | OCC_240 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement in Loc. 82.102.124,126,127,129 | 08/Aug/2026 | 8:00 | 08/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Intimation to Assam
83 | OCC_240 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Disc changing & jumper repairing at T/Loc-7 | 08/Aug/2026 | 08:00 | 08/Aug/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Intimation to Assam
84 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 08/Aug/2026 | 08:00 | 08/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
85 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 09/Aug/2026 | 09:00 | 09/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Udaipur-Palatana ,132kV Monarchak - Rokhia, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
86 | OCC_240 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 19/Aug/2026 | 09:00 | 19/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
87 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 09/Aug/2026 | 08:00 | 09/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
88 | OCC_240 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 10/Aug/2026 | 10:00 | 10/Aug/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
89 | OCC_240 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE, LOC 01-65 | 10/Aug/2026 | 8:00 | 10/Aug/2026 | 15:00 | AGM NAGAON T&T & agm mni | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
90 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work | 10/Aug/2026 | 09:00 | 10/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. SD may be availed after restoration of 132kV PK Bari-Manu line. Intimation to Indigrid
91 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work | 10/Aug/2026 | 09:00 | 10/Aug/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
92 | OCC_240 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 328 TO 284 | 10/Aug/2026 | 7:00 | 10/Aug/2026 | 15:00 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line.
93 | OCC_240 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Imphal TLM, Loc No- 68,69,102115, 116,131,132 | 10/Aug/2026 | 7:00 | 10/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
94 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 10/Aug/2026 | 08:00 | 10/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
95 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
96 | OCC_240 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
97 | OCC_240 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | CORRIDOR CLEANING | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 | AGM T&T GOALPARA | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
98 | OCC_240 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 | RE GLG | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
99 | OCC_240 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING LOC 1 TO 108 | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link & 132 Rupai -Margarita -Tinsukia link
100 | OCC_240 | POWERGRID | 220 KV MISA 1 BAY AT SAMAGURI | C | For CB Mechanism overhauling. (Line may be charged through TBC) | 11/Aug/2026 | 09:00 | 13/Aug/2026 | 17:00 |  | Sd may be availed subject to no outage of elements | SD may be deferred due to high demand in NER
101 | OCC_240 | POWERGRID | MAIN BAY (416) OF IMPHAL(PG) - 400KV - BUS 2 FUTURE @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 11/Aug/2026 | 09:00 | 11/Aug/2026 | 16:00 |  | SD may be availed
102 | OCC_240 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 3 TO 27 | 11/Aug/2026 | 08:30 | 11/Aug/2026 | 16:30 | AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
103 | OCC_240 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Imphal TLM, Loc No- 68,69,102115, 116,131,132 | 11/Aug/2026 | 7:00 | 11/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
104 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 11/Aug/2026 | 08:00 | 11/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
105 | OCC_240 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENSANCE | 11/Aug/2026 | 08:00 | 11/Aug/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
106 | OCC_240 | POWERGRID | 400 KV BISWANATH CHARIALI I & 400 KV MISA I (411)AT BALIPARA | C | DAC overhauling to rectify high CRM value of R phase of old ABB make pneumatic breaker | 11/Aug/2026 | 08:00 | 14/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of main bay of Balipara-Misa I @Balipara-400kV & main bay of Balipara-Biswanath Chariali I@Balipara-400kV
107 | OCC_240 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING LOC 36 TO 82 | 12/Aug/2026 | 9:00 | 12/Aug/2026 | 16:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
108 | OCC_240 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 12/Aug/2026 | 10:00 | 12/Aug/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
109 | OCC_240 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 102 to 100. | 12/Aug/2026 | 10:00 | 12/Aug/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
110 | OCC_240 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work | 12/Aug/2026 | 09:00 | 12/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
111 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 55,59,101,112 | 12/Aug/2026 | 09:00 | 12/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
112 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | AR in Non-Auto required for work in other circuit. | 12/Aug/2026 | 09:00 | 12/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
113 | OCC_240 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 12/Aug/2026 | 09:00 | 12/Aug/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
114 | OCC_240 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 403 TO 358 | 12/Aug/2026 | 7:00 | 12/Aug/2026 | 15:00 | AGM SSJI | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link., 220kV Balipara - Sonabil D/C and 220kV Misa - Samaguri D/C
115 | OCC_240 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Maintenance Work | 12/Aug/2026 | 08:00 | 12/Aug/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
116 | OCC_240 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Maintenance Work | 12/Aug/2026 | 08:00 | 12/Aug/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
117 | OCC_240 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | Rectification of Shut Down nature defects (Jumper defect, VD damage etc.) at various locations. | 12/Aug/2026 | 7:00 | 12/Aug/2026 | 16:00 |  | SD may be availed subjected to availability of 220KV-MARIANI (PG)-MOKOKCHUNG-1, Dimapur-Doyang-Mokokchung link
118 | OCC_240 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | AR Non-Auto required for work in other circuit. | 12/Aug/2026 | 7:00 | 12/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
119 | OCC_240 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Imphal TLM, Loc No- 68,69,102115, 116,131,132 | 14/Aug/2026 | 7:00 | 14/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
120 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 12/Aug/2026 | 7:00 | 12/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
121 | OCC_240 | POWERGRID | MARIANI (PG) - 220KV - BUS 2 | D | For testing of trip transfer logic with 220KV New Mariani-Mokokchung-2(208L) | 08/Aug/2026 | 7:00 | 08/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of other bus and all the elements needs to be transferred to other bus, Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220/132kv ICTs at Mariani(AS), 220kv Mariani(AS)-Samaguri, 220kV Mariani(PG)-Kathalguri-Mariani(AS) link, 220kv AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link, 220kV Kathalguri-Namsai D/C needs to be maintained. Dimapur-Doyang-Mokokchung(NL)-Mokokchung, 132kv Kohima-Meluri-Tuensanf-Mokokchung(NL)-Mokokchung link also needs to be present. Upper Assam Import gate flow to be kept within 140MW
122 | OCC_240 | AEGCL | 400KV/220KV AZARA-ICT-2 | D | ROUTINE BAY MAINTENANCE | 12/Aug/2026 | 07:00 | 12/Aug/2026 | 16:00 | AGM MIRZA | SD may be availed sibject to availability of 400/220kV ICT 1 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link | SD may be deferred due to high demand in NER
123 | OCC_240 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | LINE MAINTENANCE & CORRIDOR CLEANING | 13/Aug/2026 | 10:00 | 13/Aug/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
124 | OCC_240 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 13/Aug/2026 | 10:00 | 13/Aug/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, and 220kV Mawngap - Killing D/C shall be kept in service. Consent from Meghalaya.
125 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work | 13/Aug/2026 | 09:00 | 13/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
126 | OCC_240 | TSECL | 132KV-AMBASA-MANU-1 | D | Pre-Puja Maintenance Work | 13/Aug/2026 | 09:00 | 13/Aug/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
127 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 55,59,101,112 | 13/Aug/2026 | 09:00 | 13/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
128 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | AR in Non-Auto required for work in other circuit. | 13/Aug/2026 | 09:00 | 13/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
129 | OCC_240 | POWERGRID | TIE BAY (417) OF 400KV-IMPHAL(PG)-THOUBAL-1 AND FUTURE @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 13/Aug/2026 | 09:00 | 13/Aug/2026 | 16:00 |  | SD may be availed
130 | OCC_240 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 403 TO 358 | 13/Aug/2026 | 7:00 | 13/Aug/2026 | 15:00 | AGM SSJI | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link., 220kV Balipara - Sonabil D/C and 220kV Misa - Samaguri D/C | 07:00 to 15:00
131 | OCC_240 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Maintenance Work | 13/Aug/2026 | 08:00 | 13/Aug/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
132 | OCC_240 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Maintenance Work | 13/Aug/2026 | 08:00 | 13/Aug/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
133 | OCC_240 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | Rectification of Shut Down nature defects (Jumper defect, VD damage etc.) at various locations. | 13/Aug/2026 | 7:00 | 13/Aug/2026 | 16:00 |  | SD may be availed subjected to availability of 220KV-MARIANI (PG)-MOKOKCHUNG-2, Dimapur-Doyang-Mokokchung link | 07:00 to 16:00
134 | OCC_240 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | AR Non-Auto required for work in other circuit. | 13/Aug/2026 | 7:00 | 13/Aug/2026 | 16:00 |  | A/R may be kept in Non-Auto mode | 07:00 to 16:00
135 | OCC_240 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Imphal TLM, Loc No- 68,69,102115, 116,131,132 | 13/Aug/2026 | 7:00 | 13/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S | 07:00 to 16:00
136 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 13/Aug/2026 | 08:00 | 13/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
137 | OCC_240 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 13/Aug/2026 | 08:00 | 13/Aug/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
138 | OCC_240 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work | 14/Aug/2026 | 09:00 | 14/Aug/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
139 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 55,59,101,112 | 14/Aug/2026 | 09:00 | 14/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
140 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | AR in Non-Auto required for work in other circuit. | 14/Aug/2026 | 09:00 | 14/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
141 | OCC_240 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE | 14/Aug/2026 | 08:00 | 14/Aug/2026 | 16:00 | AGM NAGAON T&T & agm mni | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
142 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 14/Aug/2026 | 08:00 | 14/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
143 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 60,64,101,116,166 | 15/Aug/2026 | 09:00 | 15/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
144 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | AR in Non-Auto required for work in other circuit. | 15/Aug/2026 | 09:00 | 15/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
145 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 15/Aug/2026 | 08:00 | 15/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
146 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
147 | OCC_240 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
148 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
149 | OCC_240 | TSECL | 132KV-BODHJUNGNAGAR-JIRANIA-1 | D | Pre-Puja Maintenance Work | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
150 | OCC_240 | TSECL | BUDHJANGNAGAR - 132KV - BUS 1 | D | Pre-Puja Maintenance Work | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
151 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 60,64,101,116,166 | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
152 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | AR in Non-Auto required for work in other circuit. | 16/Aug/2026 | 09:00 | 16/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
153 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 16/Aug/2026 | 08:00 | 16/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
154 | OCC_240 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | D | PREVENTIVE MAINTENANCE | 17/Aug/2026 | 7:00 | 17/Aug/2026 | 14:00 | AGM NAGAON T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
155 | OCC_240 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Jungle Clerance | 17/Aug/2026 | 8:00 | 17/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
156 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Pre-Puja Maintenance Work | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
157 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
158 | OCC_240 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
159 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 60,64,101,116,166 | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
160 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | AR in Non-Auto required for work in other circuit. | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
161 | OCC_240 | POWERGRID | BUS COUPLER BAY () OF BONGAIGAON(PG) - 220KV - BUS 1 AND BONGAIGAON(PG) - 220KV - BUS 2 @BONGAIGAON - 220KV | D | AMP of bay equipment | 17/Aug/2026 | 09:00 | 17/Aug/2026 | 17:00 |  | SD may be availed. Elements to be segretted properly in both the buses. Bus 1: Ict-1, Salakati 1 & Bus 2: ICT-2 , Salakati 2
162 | OCC_240 | POWERGRID | 220KV-AGBPP-MARIANI (PG) | D | AMP of 206 bay equipment at Mariani S/S | 17/Aug/2026 | 08:00 | 17/Aug/2026 | 16:00 |  | SD may be availed subjected to availability of all these links as well as availability of 220 kV AGBPP-Mariani(AS) line . Under N-1 condition, Gate flow should be monitored and shall be maintained below 265 MW(during solar period) and 255 MW (during non-solar period) for safe and reliable grid operation. S/D may be availed. During SD period, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur link.RELIABILITY OF THE SYSTEM IS REDUCED. Intimation to NEEPCO
163 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 17/Aug/2026 | 08:00 | 17/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
164 | OCC_240 | POWERGRID | 400 KV BONGAIGAON I & 400 KV BISWANATH CHARIALI III (414)AT BALIPARA | C | For Mechanism Drive overhauling of old ABB make pneumatic breaker along with Auxiliary Switch replacement | 17/Aug/2026 | 08:00 | 20/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of main bay of 400kV Bongaigaon-Balipara I@Balipara-400kV & main bay of 400kV Bongaigaon-Biswanath Chariali III @Balipara-400kV
165 | OCC_240 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | D | PREVENTIVE MAINTENANCE | 18/Aug/2026 | 7:00 | 18/Aug/2026 | 14:00 | AGM NAGAON T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
166 | OCC_240 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Jungle Clerance | 18/Aug/2026 | 8:00 | 18/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
167 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work | 18/Aug/2026 | 09:00 | 18/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
168 | OCC_240 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work | 18/Aug/2026 | 09:00 | 18/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
169 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Nirjuli TLM, Loc No- 60,64,101,116,166 | 18/Aug/2026 | 09:00 | 18/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred
170 | OCC_240 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | AR in Non-Auto required for work in other circuit. | 18/Aug/2026 | 09:00 | 18/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode | SD deferred
171 | OCC_240 | POWERGRID | MAIN BAY (418) OF 400KV-IMPHAL(PG)-THOUBAL-1 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 18/Aug/2026 | 09:00 | 18/Aug/2026 | 16:00 |  | SD may be availed
172 | OCC_240 | POWERGRID | KUMARGHAT - 132KV - BUS 1 | D | Warranty Test for Bus Coupler Bay | 18/Aug/2026 | 8:00 | 18/Aug/2026 | 16:00 |  | SD may be availed Subject to the availability of 132kV Badarpur-Kolasib-Aizawl link, 132kV Badarpur-Karimganj line and 132kV Jiribam(PG)-Tipaimukh-Aizawl link
173 | OCC_240 | POWERGRID | BUS COUPLER BAY () OF KUMARGHAT - 132KV - BUS 1 AND KUMARGHAT - 132KV - BUS 2 @KUMARGHAT - 132KV | D | Warranty Test for Bus Coupler Bay | 18/Aug/2026 | 8:00 | 18/Aug/2026 | 16:00 |  | SD may be availed. All the elements may be kept in one Bus
174 | OCC_240 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 229 TO 261 | 18/Aug/2026 | 7:00 | 18/Aug/2026 | 15:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
175 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 18/Aug/2026 | 08:00 | 18/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
176 | OCC_240 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 334 | 18/Aug/2026 | 08:00 | 18/Aug/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
177 | OCC_240 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENSANCE | 18/Aug/2026 | 08:00 | 18/Aug/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
178 | OCC_240 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 150-198 | 18/Aug/2026 | 08:00 | 18/Aug/2026 | 15:00 | AGM NLK | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
179 | OCC_240 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 237 TO 162 | 18/Aug/2026 | 07:00 | 18/Aug/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
180 | OCC_240 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 119 to 117. | 19/Aug/2026 | 10:00 | 19/Aug/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
181 | OCC_240 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 19/Aug/2026 | 8:00 | 19/Aug/2026 | 15:00 | AGM T&T GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
182 | OCC_240 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-2 | D | Relay testing 1. Differential Relay – P645 2. REF – P643 3. Backup Impedance- P442 4. Backup O/C E/F (IV)-P141 5. Backup O/C E/F (HV)-P141 | 19/Aug/2026 | 8:00 | 19/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Misa-Diampur-I ckt & 132kV Dimapur - Imphal
183 | OCC_240 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Maintenance Work | 19/Aug/2026 | 08:00 | 19/Aug/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
184 | OCC_240 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM, Loc No-34,46,73,87 | 19/Aug/2026 | 7:00 | 19/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 2, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link. Intimation to INDIGRID
185 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 19/Aug/2026 | 08:00 | 19/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
186 | OCC_240 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Maintenance Work | 19/Aug/2026 | 08:00 | 19/Aug/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
187 | OCC_240 | AEGCL | 400KV-AZARA-BONGAIGAON-1 | D | ROUTINE BAY MAINTENANCE | 02/Aug/2026 | 07:00 | 02/Aug/2026 | 11:00 | AGM MIRZA | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon. The line is also approved under PNOCC for 01-08-2026 from 07:00 to 11:00 | 02/Aug/2026 07:00 to 11:00
188 | OCC_240 | AEGCL | 132KV-NTPS-TINSUKIA-1 | D | CORRIDOR CLEANING LOC 1 TO 41 | 20/Aug/2026 | 9:00 | 20/Aug/2026 | 16:00 | AGM TSK | SD may be availed subject to the availability of 220kV Tinsukia-NRPP-NTPS link and 220kV NTPS-Amguri-Mariani(AS) link
189 | OCC_240 | NETCL | 400KV-AZARA-SILCHAR | D | Replacement of rusted Jumper Cone N&B, Tightening of loose Jumper Cone/ CC Ring/ Arching Horn N&B etc. | 05/Aug/2026 | 10:00 | 05/Aug/2026 | 13:00 | Put up for approval in the 240th OCCM. | S/D may be availed subject to the availability of 400kV Bongaigaon-Azara, 220kV Agia BTPS D/C, Salakati-BTPS D/C and 400kV Bongaiagon-Killing-Silchar link. Consent from Assam and Intimation to NERTS | 05/Aug/2026
190 | OCC_240 | AEGCL | 220KV-AGIA-AZARA-1 ( 132kV Agia-Chaygaon line) | D | CORRIDOR CLEANING | 20/Aug/2026 | 8:00 | 20/Aug/2026 | 15:00 | AGM T&T GOALPARA | S/D may be availed. 220 kV Agia - Boko - Mirza link to be kept in service. Also, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/s.
191 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work | 19/Aug/2026 | 09:00 | 19/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV SM Nagar-Bodhjunagar-SM Nagar(TE) link
192 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work | 20/Aug/2026 | 09:00 | 20/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. SD may be availed after restoration of 132kV PK Bari-Manu line. Intimation to Indigrid
193 | OCC_240 | POWERGRID | 220KV/132KV MOKOKCHUNG (PG)-ICT-3 | D | 1.Warranty test/ AMP of 220 kV Bay Equipment. 2.Warranty test/ AMP of 132 kV Bay Equipment. 3.AMP of ICT-III. 4.Oil Top-up of ICT-III, R and Y phase. 5.05 Nos Relay testing as per AMP Schedule. | 20/Aug/2026 | 8:00 | 20/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-2 of Mokokchung to maintained below 40 MW.
194 | OCC_240 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Maintenance Work | 20/Aug/2026 | 08:00 | 20/Aug/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
195 | OCC_240 | POWERGRID | 132KV-IMPHAL-LOKTAK-1 | C | To facilitate stringing works between existing Tower No. 101 to new Tower No. 102 (newly diverted section for Railway diversion) and between new Tower No. 10/0 (newly diverted section for Railway diversion) to existing Tower No. 114 of 132kV LOKTAK(NHPC)-IMPHAL TL under Imphal TLM. | 20/Aug/2026 | 08:00 | 26/Aug/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Loktak – Jiribam(PG) and 132kV Loktak – Ningthoukhong. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period. Consent from NHPC | SD deferred
196 | OCC_240 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM, Loc No-34,46,73,87 | 20/Aug/2026 | 7:00 | 20/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 2, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link. Intimation to INDIGRID
197 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 20/Aug/2026 | 08:00 | 20/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
198 | OCC_240 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 20/Aug/2026 | 08:00 | 20/Aug/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
199 | OCC_240 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Maintenance Work | 20/Aug/2026 | 08:00 | 20/Aug/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.
200 | OCC_240 | POWERGRID | 400KV/220KV MARIANI (PG)-ICT-1 | D | Warranty test of 400KV Bus Reactor-1(403R) 1.Bushing Tan delta & capacitance test 2.Winding Tan delta & capacitance test 3.Core Insulation test 4.Mechanical protection checking 5.Cable IR etc. | 20/Aug/2026 | 08:00 | 20/Aug/2026 | 16:00 |  | Sd may be availed subject to availability of 400/220kV Mariani(PG) ICT-2
201 | OCC_240 | NETCL | 400KV-AZARA-BONGAIGAON-1 | D | Replacement of rusted Jumper Cone N&B, Tightening of loose Jumper Cone/ CC Ring/ Arching Horn N&B etc. | 02/Aug/2026 | 7:00 | 02/Aug/2026 | 10:00 | Put up for approval in the 240th OCCM. | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon. SD may be deferred if NER demand is high in real time | 02/Aug/2026 07:00 to 10:00
202 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work | 21/Aug/2026 | 09:00 | 21/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line. Intimation to INDIGRID
203 | OCC_240 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Pre-Puja Maintenance Work | 21/Aug/2026 | 09:00 | 21/Aug/2026 | 16:00 |  | SD may be availed
204 | OCC_240 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-1 | D | 1. Differential Relay – P645 2. REF – P643 3. Backup Impedance- P442 4. Backup O/C E/F (IV)-P141 5. Backup O/C E/F (HV)-P141 | 22/Aug/2026 | 8:00 | 22/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Misa-Diampur-II ckt and 132kV Dimapur - Imphal | 22/Aug/2026 08:00 to 16:00
205 | OCC_240 | POWERGRID | 220KV/132KV MOKOKCHUNG (PG)-ICT-3 | D | 1.Warranty test/ AMP of 220 kV Bay Equipment. 2.Warranty test/ AMP of 132 kV Bay Equipment. 3.AMP of ICT-III. 4.Oil Top-up of ICT-III, R and Y phase. 5.05 Nos Relay testing as per AMP Schedule. | 21/Aug/2026 | 8:00 | 21/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-2 of Mokokchung to maintained below 40 MW.
206 | OCC_240 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-2 | D | AMP of Bay Equipments. | 21/Aug/2026 | 7:00 | 21/Aug/2026 | 16:00 |  | SD may be availed subject to the availabilityof 132kV Surajmaninagar-Comilla 1, NLDC consent is required
207 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 21/Aug/2026 | 08:00 | 21/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
208 | OCC_240 | POWERGRID | AIZWAL - 132KV B/R 1 | D | 1.Warranty Testing of Reactor GIS Bay. 2.BUS Reactor AMP. 3. LA IR, all applicable tightening works. 4. Relay Testing. | 21/Aug/2026 | 08:00 | 21/Aug/2026 | 17:00 |  | SD may be availed
209 | OCC_240 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work | 22/Aug/2026 | 8:00 | 22/Aug/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line | 08:00 to 15:00
210 | OCC_240 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work | 22/Aug/2026 | 09:00 | 22/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
211 | OCC_240 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work | 22/Aug/2026 | 09:00 | 22/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
212 | OCC_240 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Jungle Clearance at T/Loc-51 to 54 | 22/Aug/2026 | 08:00 | 22/Aug/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Intimation to Assam
213 | OCC_240 | POWERGRID | 132KV-SURAJMANI NAGAR-COMILLA(BANGLADESH)-1 | D | AMP of Bay Equipments. | 22/Aug/2026 | 7:00 | 22/Aug/2026 | 16:00 |  | SD may be availed subject to the availabilityof 132kV Surajmaninagar-Comilla 2, NLDC consent is required | 07:00 to 16:00
214 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 22/Aug/2026 | 08:00 | 22/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
215 | OCC_240 | TSECL | DHARMANAGAR (MISSION TILLA) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work | 23/Aug/2026 | 09:00 | 23/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV Hailakandi-Dullavcherra link. Intimation to Assam is required.
216 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work | 23/Aug/2026 | 09:00 | 23/Aug/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
217 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work | 23/Aug/2026 | 09:00 | 23/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
218 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 23/Aug/2026 | 08:00 | 23/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
219 | OCC_240 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING & BAY MAINTENANCE | 23/Aug/2026 | 7:00 | 23/Aug/2026 | 14:00 | AGM T&T GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high | 23/Aug/2026 07:00 to 14:00
220 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work | 24/Aug/2026 | 09:00 | 24/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
221 | OCC_240 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work | 24/Aug/2026 | 09:00 | 24/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
222 | OCC_240 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM, Loc No- 92,68,34,35. | 24/Aug/2026 | 7:00 | 24/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 1, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link. Intimation to INDIGRID | 07:00 to 16:00
223 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 24/Aug/2026 | 08:00 | 24/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
224 | OCC_240 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 334 | 24/Aug/2026 | 08:00 | 24/Aug/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
225 | OCC_240 | AEGCL | 132KV-GOHPUR-NALKATA-1 | C | SHIFTING 132kV AIS BAY TO GIS BAY | 24/Aug/2026 | 08:00 | 12/Sep/2026 | 18:00 | RE GOHPUR | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
226 | OCC_240 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 1 | D | AMP Works of Bus-1A | 24/Aug/2026 | 08:00 | 24/Aug/2026 | 17:00 | Bus-1 has sectionaliser and it's divided into Bus 1A & Bus 1B. This is for Bus-1A | SD may be availed subject to the availability of Bus-2A. All the dias should be in service | Sd deferred due to high NER demand and hydro generation
227 | OCC_240 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work | 25/Aug/2026 | 09:00 | 25/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link.
228 | OCC_240 | TSECL | 132KV-AMBASA-MANU-1 | D | Pre-Puja Maintenance Work | 25/Aug/2026 | 09:00 | 25/Aug/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
229 | OCC_240 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 328 TO 284 | 25/Aug/2026 | 7:00 | 25/Aug/2026 | 15:00 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line.
230 | OCC_240 | POWERGRID | 400KV-SILCHAR-PK BARI (STERLITE)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Silchar TLM, Loc No- 92,68,34,35. | 25/Aug/2026 | 7:00 | 25/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 400kV Silchar-Pk Bari ckt 1, 400kv Palatana-Silchar D/C and 400kv Palatana-SM Nagar-PK bari link. Intimation to INDIGRID
231 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 25/Aug/2026 | 08:00 | 25/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
232 | OCC_240 | POWERGRID | 220KV/132KV BALIPARA-ICT-1 | D | To replace the isolator male/female contacts of 219-89A isolator | 25/Aug/2026 | 7:00 | 25/Aug/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kv Kameng-Khupi-Tenga link. Consent from AP is required
233 | OCC_240 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 2 | D | AMP Works of Bus-2A | 25/Aug/2026 | 08:00 | 25/Aug/2026 | 17:00 | Bus-2 has sectionaliser and it's divided into Bus 2A & Bus 2B. This is for Bus-2A | SD may be availed subject to the availability of Bus-1A. All the dias should be in service | Sd deferred due to high NER demand and hydro generation
234 | OCC_240 | POWERGRID | BALIPARA - 220KV - BUS 1 | D | To replace the isolator male/female contacts of 219-89A isolator | 22/Aug/2026 | 7:00 | 22/Aug/2026 | 15:00 |  | SD may be availed subject to no ouatge of elements. All elements may be shifted to other bus prior to shutdown. | 22/Aug/2026 07:00 to 15:00
235 | OCC_240 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 237 TO 162 | 25/Aug/2026 | 07:00 | 25/Aug/2026 | 16:00 | AGM SSJI & agm smg | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
236 | OCC_240 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 116 to 114. | 26/Aug/2026 | 10:00 | 26/Aug/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
237 | OCC_240 | POWERGRID | BTPS(NTPC) II (FUTURE) & 2X 80 MVAR BUS REACTOR III AND IVAT BONGAIGAON | D | AMP of Bay Equipments | 26/Aug/2026 | 09:00 | 26/Aug/2026 | 17:00 |  | SD may be availed subject to the availability of NTPC- Bongaigaon ckt 1 and Ckt 2 must be charged though main bay
238 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 26/Aug/2026 | 08:00 | 26/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
239 | OCC_240 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 1 | D | AMP Works of Bus-1B | 26/Aug/2026 | 08:00 | 26/Aug/2026 | 17:00 | Bus-1 has sectionaliser and it's divided into Bus 1A & Bus 1B. This is for Bus-1B | SD may be availed subject to the availability of Bus-2B. All the dias should be in service | Sd deferred due to high NER demand and hydro generation
240 | OCC_240 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING LOC 74 TO 112 | 27/Aug/2026 | 10:00 | 27/Aug/2026 | 16:00 | AGM TSK | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
241 | OCC_240 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING & BAY MAINTENANCE | 30/Aug/2026 | 7:00 | 30/Aug/2026 | 14:00 | AGM T&T GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
242 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work | 27/Aug/2026 | 09:00 | 27/Aug/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
243 | OCC_240 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work | 27/Aug/2026 | 09:00 | 27/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
244 | OCC_240 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 27/Aug/2026 | 09:00 | 27/Aug/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
245 | OCC_240 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Badarpur TLM, Loc No- 239,240,243,244,268,269. | 27/Aug/2026 | 7:00 | 27/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Consent from Mizoram
246 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 27/Aug/2026 | 08:00 | 27/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
247 | OCC_240 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 2 | D | AMP Works of Bus-2B | 27/Aug/2026 | 08:00 | 27/Aug/2026 | 17:00 | Bus-2 has sectionaliser and it's divided into Bus 2A & Bus 2B. This is for Bus-2B | SD may be availed subject to the availability of Bus-1B. All the dias should be in service | Sd deferred due to high NER demand and hydro generation
248 | OCC_240 | MEPTCL | LUMSNONG - 132KV - BUS 1 | D | Maintenance Work | 28/Aug/2026 | 8:00 | 28/Aug/2026 | 15:00 | Avail | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Assam.
249 | OCC_240 | MEPTCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | Maintenance Work | 28/Aug/2026 | 8:00 | 28/Aug/2026 | 15:00 | Avail | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Assam.
250 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work | 28/Aug/2026 | 09:00 | 28/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
251 | OCC_240 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work | 28/Aug/2026 | 09:00 | 28/Aug/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
252 | OCC_240 | POWERGRID | SILCHAR - 400KV - BUS 2 | D | 400KV BUSBAR RELAY TESTING AT SILCHAR SS | 28/Aug/2026 | 7:00 | 28/Aug/2026 | 15:00 |  | SD may be availed. All the dias should be in service. 400kV Palatana - SM Nagar - PK Bari - Silchar link, 400kV Palatana - Silchar D/C and 400kV Mirza - Silchar link should be available.
253 | OCC_240 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 209 TO 215 | 28/Aug/2026 | 7:00 | 28/Aug/2026 | 15:00 | AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
254 | OCC_240 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Badarpur TLM, Loc No- 239,240,243,244,268,269. | 28/Aug/2026 | 7:00 | 28/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Consent from Mizoram
255 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 28/Aug/2026 | 08:00 | 28/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
256 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work | 29/Aug/2026 | 09:00 | 29/Aug/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. SD may be availed after charging of 132kV PK Bari-Manu line.
257 | OCC_240 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations by Badarpur TLM, Loc No- 239,240,243,244,268,269. | 29/Aug/2026 | 7:00 | 29/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Consent from Mizoram
258 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 29/Aug/2026 | 08:00 | 29/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
259 | OCC_240 | POWERGRID | 400KV/220KV MARIANI (PG)-ICT-2 | D | Electromechanical Relay Replacement with Numerical Relay and Integration on the same for Body Protection of ICTs | 29/Aug/2026 | 08:00 | 29/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 400/220kV ICT I at Mariani.
260 | OCC_240 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work | 30/Aug/2026 | 09:00 | 30/Aug/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
261 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 30/Aug/2026 | 08:00 | 30/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
262 | OCC_240 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work | 31/Aug/2026 | 09:00 | 31/Aug/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. SD may be availed after restoration of 132kV PK Bari-Manu line. Intimation to Indigrid
263 | OCC_240 | POWERGRID | A/R of 132KV-JIRIBAM(PG)-TIPAIMUMK-1 | D | AR in Non-Auto Mode Required for OPGW installation. Shutdown of the Line not Required. | 31/Aug/2026 | 08:00 | 31/Aug/2026 | 17:00 |  | A/R may be kept in Non-Auto mode
264 | OCC_240 | POWERGRID | MARIANI (PG) - 400KV B/R 1 | D | Warranty test of 400KV Bus Reactor-1(403R) 1.Bushing Tan delta & capacitance test 2.Winding Tan delta & capacitance test 3.Core Insulation test 4.Mechanical protection checking 5.Cable IR etc. | 31/Aug/2026 | 08:00 | 31/Aug/2026 | 16:00 |  | SD may be availed