## Sheet1
Sl no. | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Study Comments | Remarks
1 | OCC_241 | POWERGRID | MAIN BAY (113) OF 132KV-ROING-DAMBUK-1 @ROING - 132KV | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 01/Sep/2026 | 14:00 | 01/Sep/2026 | 18:00 |  | SD may be availed
2 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 01/Sep/2026 | 09:00 | 01/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
3 | OCC_241 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 01/Sep/2026 | 09:00 | 01/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 190 MW during the shutdown period. Intimation to Indigrid
4 | OCC_241 | POWERGRID | 132KV-HAFLONG-JIRIBAM-1 | C | for carrying out stringing work and shifting the line from the existing ERS1 & ERS2 to the newly tower | 01/Sep/2026 | 08:00 | 10/Sep/2026 | 17:00 |  | SD may be availed subjected to availability of 132kV Khandong - Umrangsho - Haflong (PG), 132kV Jiribam-Pailapool, Jiribam-Loktak & Jiribam-Tipaimukh-Aizwal link.FTC procedure to be followed before charging of the line
5 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 01/Sep/2026 | 08:00 | 01/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
6 | OCC_241 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING LOC 77-80 | 01/Sep/2026 | 08:00 | 01/Sep/2026 | 16:00 | RE LEDO | S/D may be availed subject to the availability of 132kV Tinsukia-Rupai and 132kV Tinsukia-Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
7 | OCC_241 | POWERGRID | 132KV-CHAPAKHOWA-ROING-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 02/Sep/2026 | 12:00 | 02/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-1, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
8 | OCC_241 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 02/Sep/2026 | 10:00 | 02/Sep/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
9 | OCC_241 | POWERGRID | 132KV-CHAPAKHOWA-ROING-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 02/Sep/2026 | 7:00 | 02/Sep/2026 | 11:00 |  | SD may be availed subject to availability of 132kV Roing - Chapakhowa ckt-2, Roing-Tezu-Namsai-Kathalguri link and 132kV Rupai - Chapakhowa line. Consent from Assam
10 | OCC_241 | POWERGRID | 132KV-SILCHAR-BADARPUR-1 | D | 132KV BAY AMP WORK AT SILCHAR SS. | 02/Sep/2026 | 09:00 | 02/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 132KV-SILCHAR-BADARPUR-2.
11 | OCC_241 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 02/Sep/2026 | 09:00 | 02/Sep/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. . Intimation to INDIGRID
12 | OCC_241 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING | 06/Sep/2026 | 7:00 | 06/Sep/2026 | 14:00 | AGM GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high
13 | OCC_241 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING LOC 1 TO 38 | 02/Sep/2026 | 09:00 | 02/Sep/2026 | 16:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
14 | OCC_241 | POWERGRID | 220KV-AGBPP-MARIANI (AS)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 247,270 by Mariani TLM | 04/Sep/2026 | 08:00 | 04/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 220kV AGBPP-Mariani(PG)-Mariani(As) link, 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(As) link, 220kV Mariani-Samaguri line & 132kV Mariani-Golaghat-Sarupathar-Bokajan-Dimapur link, Upper assam gate flow to be maintained within 260 MW. Consent from Assam
15 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 02/Sep/2026 | 7:00 | 02/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
16 | OCC_241 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 74 TO 35 | 02/Sep/2026 | 08:00 | 02/Sep/2026 | 16:00 | AGM SSJI | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
17 | OCC_241 | POWERGRID | 132KV-KHLIEHRIAT(ME)-NEIGRIHMS-1 | C | Tower Shifting by MePTCL | 15/Sep/2026 | 9:00 | 16/Sep/2026 | 16:00 | Tower Shifting by MePTCL | SD may be availed subject to availabilty of 132kV Umiam-1-Umiam-nehu link and 132kV Umiam-1-Mawlai-Nehu link to be in service.220 kV Killing-Mawngap D/C to be in service. 132kV Khelihriat-Mustem line loading to be maintained by Meghalaya. Consent from Meghalaya is required.
18 | OCC_241 | POWERGRID | 132KV-KHLIEHRIAT(ME)-NEIGRIHMS-1 | C | Data Shutdown required for Tower Shifting by MePTCL | 15/Sep/2026 | 9:00 | 16/Sep/2026 | 16:00 | Data Shutdown required for Tower Shifting by MePTCL | For Central Sector: NEHU-NERLDC Shillong will be alternate path.
19 | OCC_241 | POWERGRID | ROING - 132KV B/R 1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 03/Sep/2026 | 14:00 | 03/Sep/2026 | 18:00 |  | SD may be availed
20 | OCC_241 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 99 to 97. | 03/Sep/2026 | 10:00 | 03/Sep/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
21 | OCC_241 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Sep/2026 | 10:00 | 03/Sep/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya
22 | OCC_241 | POWERGRID | 132KV-MELRIAT-SINHMUI-2 | D | AMP of bay equipment | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 16:00 |  | Sd may be availed subject to availability of 132kV Melriat - Shimuii I. Consent from Mizoram
23 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
24 | OCC_241 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link. Intimation to INDIGRID
25 | OCC_241 | POWERGRID | 132KV/33KV ROING-ICT-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 13:00 |  | SD may be availed subject to the availability of other ICT. Consented from AP
26 | OCC_241 | POWERGRID | 400 KV BALIPARA 1 BAY(WITH 63 MVAR LINE REACTOR) (413) AT BONGAIGAON | D | AMP of Bay Equipments | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 17:00 | ONLY MAIN BAY(413) BALIPARA-1 AT BONGAIGAON SHUTDOWN REQUIRED | SD may be availed subject to the availability of Main bay of 400kV Alipurduar-Bongaigaon 1 @Bongaigaon-400kV and Tie bay of 400kV Alipurduar-Bingaigaon 1 and 400kV Balipara-Bongaigaon 1 @Bongaigaon-400kV
27 | OCC_241 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | D | CORRIDOR CLEANING LOC 30-35 | 03/Sep/2026 | 09:00 | 03/Sep/2026 | 16:00 | RE LEDO | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and kathalguri-Namsai-Tezu-Roing-Chapakhow-Rupai link
28 | OCC_241 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 01/Sep/2026 | 09:00 | 01/Sep/2026 | 16:00 | RE GLG | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
29 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-3 | D | For attending S/D related defects viz. CC Ring displacement, arching horn fitting etc. by Balipara TLM | 03/Sep/2026 | 08:00 | 03/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-BALIPARA-1, 2 & 4.
30 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 03/Sep/2026 | 08:00 | 03/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
31 | OCC_241 | POWERGRID | IMPHAL - 132KV B/R 1 | D | AMP of bay equipment | 03/Sep/2026 | 08:00 | 03/Sep/2026 | 17:00 |  | SD may be availed
32 | OCC_241 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 03/Sep/2026 | 08:00 | 03/Sep/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
33 | OCC_241 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | CORRIDOR CLEANING & MAINTENANCE | 03/Sep/2026 | 08:00 | 03/Sep/2026 | 16:00 | AGM SALAKATI | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
34 | OCC_241 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE BETWEEN LOC 314 TO 238 | 03/Sep/2026 | 7:00 | 03/Sep/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
35 | OCC_241 | AEGCL | AZARA - 400KV - BUS 1 | D | bus isolator allignment & routine maintenance work | 03/Sep/2026 | 07:00 | 03/Sep/2026 | 16:00 | AGM MIRZA | SD may be availed subject to no outage of elements, Tie Bay of Bongaingaon Azara & 400/220kV Azara ICT-1 to be in service,220kV BTPS-Agia D/C, 220kV Agia-Chaygaon-Azara, 220kV Agia-Boko -Azara link, 220kV Samaguri-Sonapur-Sarusjai link and 220kV Samaguri-Jawaharnagar-Sarusajai link to be in service. | SD deferred and may be availed in lean demand period.
36 | OCC_241 | POWERGRID | 132KV/33KV ROING-ICT-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 04/Sep/2026 | 09:00 | 04/Sep/2026 | 13:00 |  | SD may be availed subject to the availability of 132KV/33KV ROING-ICT-1. Consent from AP
37 | OCC_241 | POWERGRID | 132KV-DAPORIJU-ZIRO-1 | D | AMP works in the Daporijo Bay | 04/Sep/2026 | 8:00 | 04/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. Consent from AP
38 | OCC_241 | POWERGRID | 132KV-BADARPUR-PANCHGRAM (NEW)-1 | D | For bay AMP work at both the State and POWERGRID ends. | 06/Sep/2026 | 08:00 | 06/Sep/2026 | 16:00 |  | S/D may be availed subject to the availabilty of 132kV Panchgram-Lumnsnong -Khleihriat line.
39 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-4 | D | For attending S/D related defects viz. CC Ring displacement, arching horn fitting etc.by Balipara TLM | 04/Sep/2026 | 7:00 | 04/Sep/2026 | 16:00 |  | Sd may be availed subject to availability of 400kV BNC - Balipra 1,2 and 3
40 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 04/Sep/2026 | 08:00 | 04/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode, to be deferred due to PSD of 132kV Ziro-Daporijo. | SD to be deferred.
41 | OCC_241 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | C | Rectification of JB at LILO Point | 05/Sep/2026 | 15:30 | 06/Sep/2026 | 18:30 | Rectification of JB at LILO Point | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Consent from Nagaland is required
42 | OCC_241 | POWERGRID | 132KV-DIMAPUR(PG)-KOHIMA-1 | C | Data Shutdown Required for Rectification of JB at LILO Point | 05/Sep/2026 | 15:30 | 06/Sep/2026 | 18:30 | Data Shutdown Required for Rectification of JB at LILO Point | No alternate path for Kohima.(protection link can be from powertell)
43 | OCC_241 | POWERGRID | 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 05/Sep/2026 | 13:00 | 05/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line. Consent from Nagaland
44 | OCC_241 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/Sep/2026 | 10:00 | 05/Sep/2026 | 16:00 | AGM PNG | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
45 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 05/Sep/2026 | 09:00 | 05/Sep/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
46 | OCC_241 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 05/Sep/2026 | 09:00 | 05/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
47 | OCC_241 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 1 TO 159 | 05/Sep/2026 | 09:00 | 05/Sep/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Daporizo-Basar-Along-Pasighat-Roing link. Intimation to AP and NERTS
48 | OCC_241 | POWERGRID | 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 05/Sep/2026 | 08:00 | 05/Sep/2026 | 12:00 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line. Consent from Nagaland
49 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 05/Sep/2026 | 08:00 | 05/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode, to be deferred due to PSD of 132KV-RUPAI-CHAPAKHOWA-1. | SD to be deferred.
50 | OCC_241 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 307 TO 245 | 02/Sep/2026 | 08:00 | 02/Sep/2026 | 16:00 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line,
51 | OCC_241 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 05/Sep/2026 | 08:00 | 05/Sep/2026 | 16:00 | AGM MNI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 240 MW (during solar period) and 260 MW (during non-solar period)
52 | OCC_241 | AEGCL | AZARA - 400KV - BUS 2 | D | bus isolator allignment & routine maintenance work | 05/Sep/2026 | 07:00 | 05/Sep/2026 | 16:00 | AGM MIRZA | SD may be availed subject to no outage of elements, Tie Bay of Bongaingaon Azara & 400/220kV Azara ICT-1 to be in service,220kV BTPS-Agia D/C, 220kV Agia-Chaygaon-Azara, 220kV Agia-Boko -Azara link, 220kV Samaguri-Sonapur-Sarusjai link and 220kV Samaguri-Jawaharnagar-Sarusajai link to be in service. | SD deferred and may be availed in lean demand period.
53 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 06/Sep/2026 | 09:00 | 06/Sep/2026 | 16:00 | Bus Section III | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartala-RC nagar-Pk bari D/C, 132kV Agartala-RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur-Agartala link, 132kV SMNagar(ST)-SMNagar line, 132kV SMNagar(ST)-Budhjungnagar=SMNagar line. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 170 MW during the shutdown period
54 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Pre-Puja Maintenance Work 2026 | 06/Sep/2026 | 09:00 | 06/Sep/2026 | 16:00 | Bus Section III
55 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 06/Sep/2026 | 09:00 | 06/Sep/2026 | 16:00 | Bus Section III
56 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-AGTCCPP-2 | D | Pre-Puja Maintenance Work 2026 | 06/Sep/2026 | 09:00 | 06/Sep/2026 | 16:00 | Bus Section III
57 | OCC_241 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 06/Sep/2026 | 09:00 | 06/Sep/2026 | 16:00 | Bus Section III
58 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 06/Sep/2026 | 08:00 | 06/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
59 | OCC_241 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 07/Sep/2026 | 13:00 | 07/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line. Consent from Nagaland
60 | OCC_241 | POWERGRID | 132KV-NEHU-UMIAM-1 | C | As requested by MePTCL due to OPGW Approach cable shifting from Nehu SLDC Old building to new building. O2 nos, of ULDC Link connected at nehu are : Nehu-Umiam satge 1 & Nehu- khleriat. Only Nehu shall be out during the shifting period and data of umium stage 1 and Shillong/Khliehriat shall be through alternate paths of ECI | 07/Sep/2026 | 10:30 | 09/Sep/2026 | 18:30 | As requested by MePTCL due to OPGW Approach cable shifting from Nehu SLDC Old building to new building. O2 nos, of ULDC Link connected at nehu are : Nehu-Umiam satge 1 & Nehu- khleriat. Only Nehu shall be out during the shifting period and data of umium stage 1 and Shillong/Khliehriat shall be through alternate paths of ECI | SD may be availed subject to availabilty of 132kV Khleihriat-Mustem_mawlyndep-Nehu link, 132kV Khleihriat-Neigrihms-Nehu link and 132kV Nehu-Mawlai line. Consent from Meghalaya is required. | Line SD is not required
61 | OCC_241 | POWERGRID | 132KV-NEHU-UMIAM-1 | C | Data Shutdown Required. As requested by MePTCL due to OPGW Approach cable shifting from Nehu SLDC Old building to new building. O2 nos, of ULDC Link connected at nehu are : Nehu-Umiam satge 1 & Nehu- khleriat. Only Nehu shall be out during the shifting period and data of umium stage 1 and Shillong/Khliehriat shall be through alternate paths of ECI | 07/Sep/2026 | 10:30 | 09/Sep/2026 | 18:30 | Data Shutdown Required. As requested by MePTCL due to OPGW Approach cable shifting from Nehu SLDC Old building to new building. O2 nos, of ULDC Link connected at nehu are : Nehu-Umiam satge 1 & Nehu- khleriat. Only Nehu shall be out during the shifting period and data of umium stage 1 and Shillong/Khliehriat shall be through alternate paths of ECI | Alternate Path for NERLDC Shillong: NERLDC Shillong- Khilerirat (ME)- Khilerirat (PG)-ULDC Network | Alternative route of data required need SCADA team input
62 | OCC_241 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Sep/2026 | 10:00 | 07/Sep/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
63 | OCC_241 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING LOC 1 TO 108 | 07/Sep/2026 | 10:00 | 07/Sep/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link & 132 Rupai -Margarita -Tinsukia link
64 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work 2026 | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
65 | OCC_241 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 07/Sep/2026 | 09:00 | 07/Sep/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
66 | OCC_241 | POWERGRID | TIE BAY () OF 400KV-BALIPARA-BONGAIGAON-3 AND 400KV-BALIPARA-KAMENG-2 @BALIPARA - 400KV | D | Bay Equipment AMP | 07/Sep/2026 | 09:00 | 07/Sep/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
67 | OCC_241 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING | 13/Sep/2026 | 7:00 | 13/Sep/2026 | 14:00 | AGM GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
68 | OCC_241 | POWERGRID | 132KV-IMPHAL-LOKTAK-1 | C | To facilitate stringing works between existing Tower No. 101 to new Tower No. 102 (newly diverted section for Railway diversion) and between new Tower No. 10/0 (newly diverted section for Railway diversion) to existing Tower No. 114 of 132kV LOKTAK(NHPC)-IMPHAL TL under Imphal TLM. | 07/Sep/2026 | 08:00 | 12/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Loktak – Jiribam(PG) and 132kV Loktak – Ningthoukhong. Loktak generation to be kept below 95 MW to avoid overloading of 132kV Loktak – Ningthoukhong. SPS at Loktak to be kept in ON condition during the shutdown period. Consent from NHPC | SD deferred and may be availed with Loktak R&M switchyard SD in nov'2026
69 | OCC_241 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 07/Sep/2026 | 08:00 | 07/Sep/2026 | 12:00 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line. Consent from Nagaland
70 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 07/Sep/2026 | 08:00 | 07/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode,
71 | OCC_241 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations.Loc. 233,268,282,290,293,300,327 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting.S | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link. Consent from AP
72 | OCC_241 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 39 TO 3 | 07/Sep/2026 | 08:00 | 07/Sep/2026 | 16:00 | AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
73 | OCC_241 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 65 | 07/Sep/2026 | 08:00 | 07/Sep/2026 | 16:00 | AGM MNI & AGM NGN T&T | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
74 | OCC_241 | MSPCL | 400KV/132KV THOUBAL-ICT-1 | D | monthly changeover of 3x105 MVA TRANSFORMER (R,Y & Sp phaser ICT will be charged | 08/Sep/2026 | 11:00 | 08/Sep/2026 | 13:00 | no load will be affected during the shutdown | SD may be availed subject to availability of 132kV Imphal – Yingagangpokpi-Kongba-New Thoubal – Old Thoubal – Kakching – Churachandpur – Ningthoukhong link. Manipur demand to be kept below 170 MW to avoid low voltage under n-1 contingecy of 132kV Ningthoukhong – Churachandpur II.
75 | OCC_241 | MEPTCL | 132KV-KHLIEHRIAT(ME)-KHELIEHRIAT-2 | D | Thorough checking of lines especially of nuts and bolts, checking of disc insulator and jumper clamps, where climbing of towers will be required (Loc. 1 to Loc. 204) | 08/Sep/2026 | 10:00 | 08/Sep/2026 | 16:00 | Avail | SD may be availed subject to availability of 132kV Khleihriat - Khleihriat 1, 132kV Badarpur - Panchgram - Lumshnong- Khliehriat link and 220kV Killing - Mawngap D/C. Intimation to NERTS
76 | OCC_241 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 314 by Kolasib TLM. | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 17:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
77 | OCC_241 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 23,24,26,68,69 BY NIRJULI TLM | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred and may be availed during lean hydro period. (Nov, Dec)
78 | OCC_241 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132kV SM Nagar(TE)-SM Nagar(ISTS) and 132kV Bodhjungnagar(TE)-SM Nagar(ISTS) needs to be maintained below 160MW during SD period.
79 | OCC_241 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
80 | OCC_241 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 16:00 |  | SD may be availed. Intimation to NERTS
81 | OCC_241 | POWERGRID | MAIN BAY () OF 400KV-IMPHAL(PG)-400 KV NEW KOHIMA-2 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 15:00 |  | SD may be availed subject to the availability of Main bay of 125 MVAr Bus Reactor-2@Imphal-400kV and tie bay of 125 MVAr Bus Reactor-2 and 400kV Imphal-New Kohima-2@Imphal-400kV
82 | OCC_241 | POWERGRID | 220 KV MISA 1 BAY AT SAMAGURI | C | For CB Mechanism overhauling. (Line may be charged through TBC) | 08/Sep/2026 | 09:00 | 10/Sep/2026 | 17:00 | Line may be charged through TBC | Sd may be availed subject to no outage of elements | SD deferred and may be availed during lean hydro period. (Nov, Dec)
83 | OCC_241 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 08/Sep/2026 | 09:00 | 08/Sep/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service. Intimation to NERTS
84 | OCC_241 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | C | FOR CB MECHANISM OVERHAULING WORKS. | 08/Sep/2026 | 08:00 | 13/Sep/2026 | 18:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. | SD deferred and may be availed during lean demand period.
85 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 08/Sep/2026 | 08:00 | 08/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
86 | OCC_241 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations.Loc. 233,268,282,290,293,300,327 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting.S | 15/Sep/2026 | 08:00 | 15/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link. Consent from AP
87 | OCC_241 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 08/Sep/2026 | 08:00 | 08/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of ICT II and III at Mokokching. Combined loaidng in ICT-II and ICT-III of Mokokchung to maintained below 40 MW.
88 | OCC_241 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | CORRIDOR CLEANING LOC 209 TO 238 | 08/Sep/2026 | 08:00 | 08/Sep/2026 | 16:00 | AGM GOALPARA & AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
89 | OCC_241 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | CORRIDOR CLEANING & MAINTENANCE | 08/Sep/2026 | 08:00 | 08/Sep/2026 | 16:00 | AGM SALAKATI | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
90 | OCC_241 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 209-307 | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 16:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
91 | OCC_241 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING LOC 314 TO 238 & LOC 1 TO 70 | 08/Sep/2026 | 07:00 | 08/Sep/2026 | 16:00 | AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
92 | OCC_241 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | C | Rectification of Lossy Span | 09/Sep/2026 | 10:30 | 10/Sep/2026 | 18:30 | Rectification of Lossy Span | Sd may be availed. NLDC consent is required
93 | OCC_241 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | C | Data Shutdown Required for Rectification of Lossy Span | 09/Sep/2026 | 10:30 | 10/Sep/2026 | 18:30 | Data Shutdown Required for Rectification of Lossy Span | Not required as no activer service is configured over this path.
94 | OCC_241 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | CORRIDOR CLEANING LOC 260-265 | 09/Sep/2026 | 10:00 | 09/Sep/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
95 | OCC_241 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 23,24,26,68,69 BY NIRJULI TLM | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred and may be availed during lean demand period.
96 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work 2026 | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
97 | OCC_241 | TSECL | 132KV-AMBASA-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
98 | OCC_241 | POWERGRID | TIE BAY (417) OF 400KV-BALIPARA-BONGAIGAON-2 AND 400KV-BISWANATH CHARIALI-BALIPARA-4 @BALIPARA - 400KV | D | Bay Equipment AMP | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 400kV Balipara – Bongaigaon 2 main bay and 400kV Balipara – BNC 4 main bay at Balipara
99 | OCC_241 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation Clearance | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
100 | OCC_241 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 | RE GLG | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
101 | OCC_241 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
102 | OCC_241 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 | AGM GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
103 | OCC_241 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING LOC 45 TO 82 | 09/Sep/2026 | 09:00 | 09/Sep/2026 | 16:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
104 | OCC_241 | POWERGRID | 132KV-AIZWAL-MELRIAT-1 | D | Installation of additional jumper in tower no. 1 & 2 for compliance of CC SIR by AIZWAL TLM. | 09/Sep/2026 | 7:00 | 09/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Badarpur-Kolasib-Aizawl link, 132kV Jiribam-Tipaimukh-Aizawl link and 132kV Kumarghat-Aizawl line. Under the N-1 contingency of the 132 kV Aizawl–Kolasib line, the line loading of 132kV Aizawl-Lungmual line to kept within 40 MW to avoid low voltage in the Lunglei area of the Mizoram power system. SLDC Mizoram is requested to continuously monitor and manage the low-voltage condition in real time to ensure secure system operation. Consent from Mizoram is required
105 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 09/Sep/2026 | 08:00 | 09/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
106 | OCC_241 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations.Loc. 233,268,282,290,293,300,327 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting.S | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link. Consent from AP
107 | OCC_241 | POWERGRID | MARIANI (PG) - 400KV B/R 1 | D | For LBB relay testing of 402 tie bay | 09/Sep/2026 | 08:00 | 09/Sep/2026 | 16:00 |  | SD may be availed
108 | OCC_241 | POWERGRID | MARIANI (PG) - 400KV - BUS 1 | D | For LBB relay testing of 402 tie bay | 09/Sep/2026 | 08:00 | 09/Sep/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
109 | OCC_241 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | D | Checking the hardware cum jungle clearance at Tower -1 & 2 | 09/Sep/2026 | 08:00 | 09/Sep/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
110 | OCC_241 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | D | Checking the hardware cum jungle clearance at Tower -1 & 2 | 09/Sep/2026 | 08:00 | 09/Sep/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
111 | OCC_241 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 66 TO 95 | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 16:00 | AGM MNI & AGM NGN T&T | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
112 | OCC_241 | POWERGRID | 132KV/33KV TEZU-ICT-1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 10/Sep/2026 | 14:00 | 10/Sep/2026 | 18:00 |  | SD may be availed subject to the availability of 132KV/33KV TEZU-ICT-2. Consent from AP
113 | OCC_241 | AEGCL | 220KV-SALAKATI-BTPS-2 | D | CORRIDOR CLEANING & MAINTENANCE | 10/Sep/2026 | 11:00 | 10/Sep/2026 | 13:00 | AGM SALAKATI | SD may be availed subject to availability of 220 kV BTPS-Salakati I and 220kV BTPS-BgTPP D/C line. Combined loading of 220kV BTPS-BgTPP D/C and 220kV BTPS-Salakati-2 to be kept within 540 MW. Intimation to NERTS
114 | OCC_241 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 96 to 94. | 10/Sep/2026 | 10:00 | 10/Sep/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
115 | OCC_241 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | CORRIDOR CLEANING LOC 265-273 | 10/Sep/2026 | 10:00 | 10/Sep/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
116 | OCC_241 | POWERGRID | 400KV-AZARA-BONGAIGAON-1 | D | Annual Maintenance of 421 main-bay equipment's, 421-line-bay equipment's and 421 Reactor-Bay equipment's. | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 17:00 |  | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon. SD may be deferred if NER demand is high in real time | SD deferred and may be availed during lean demand period.
117 | OCC_241 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 23,24,26,68,69 BY NIRJULI TLM | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. One Pare Generation needs to be scheduled when the combined loading of AP capital and Gohpur exceeds 170 MW. Consent from NEEPCO is required | SD deferred and may be availed during lean demand period.
118 | OCC_241 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
119 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
120 | OCC_241 | POWERGRID | MAIN BAY (403) OF 400KV/132KV IMPHAL(PG)-ICT-1 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 15:00 |  | SD may be availed
121 | OCC_241 | POWERGRID | 400 KV BYRNIHAT MAIN BAY ( WITH 63 MVAR LINE REACTOR ) (403) AT SILCHAR | D | AMP OF BAY EQUIPMENTS(406 BAY) | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 17:00 | ONLY MAIN BAY OF BYRNIHAT LINE AT SILCHAR END IS REQUIRED & IT'S BAY NO. IS 406 FOR BYRNIHAT LINE | SD may be availed
122 | OCC_241 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation Clearance | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
123 | OCC_241 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | D | Jungle Cutting at T/Loc-273-289 | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link. Intimation to Assam
124 | OCC_241 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING LOC 1 TO 108 | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 | RE RUPAI | S/D may be availed subject to the availability of 132kV Tinsukia-Rupai and 132kV Tinsukia-Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
125 | OCC_241 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 10/Sep/2026 | 09:00 | 10/Sep/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
126 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 10/Sep/2026 | 08:00 | 10/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
127 | OCC_241 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations.Loc. 233,268,282,290,293,300,327 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting.S | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link. Consent from AP
128 | OCC_241 | AEGCL | 220KV-SALAKATI-BTPS-1 | D | CORRIDOR CLEANING & MAINTENANCE | 10/Sep/2026 | 08:00 | 10/Sep/2026 | 11:00 | AGM SALAKATI | SD may be availed subject to availability of 220 kV BTPS-Salakati I and 220kV BTPS-BgTPP D/C line. Combined loading of 220kV BTPS-BgTPP D/C and 220kV BTPS-Salakati-2 to be kept within 540 MW. Intimation to NERTS
129 | OCC_241 | AEGCL | 220KV-AZARA-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 403 TO 358 | 15/Sep/2026 | 08:00 | 15/Sep/2026 | 16:00 | AGM SSJI | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai II & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link., 220kV Balipara - Sonabil D/C and 220kV Misa - Samaguri D/C
130 | OCC_241 | AEGCL | BTPS - 220KV - BUS 1 | D | bus isolator maintenance & routine maintenance | 10/Sep/2026 | 08:00 | 10/Sep/2026 | 13:00 | AGM SALAKATI | SD may be availed subject to no outage of elements.
131 | OCC_241 | POWERGRID | TEZU - 132KV B/R 1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 11/Sep/2026 | 14:00 | 11/Sep/2026 | 18:00 |  | SD may be availed
132 | OCC_241 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.82,102,124,126,127,129 BY NIRJULI TLM | 11/Sep/2026 | 8:00 | 11/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Intimation to Assam
133 | OCC_241 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 11/Sep/2026 | 09:00 | 11/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
134 | OCC_241 | TSECL | SURAJMANI NAGAR - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 11/Sep/2026 | 09:00 | 11/Sep/2026 | 16:00 |  | Sd may be availed subject to no outage of elements. All element shifted to Main Bus 2 online before taking SD. 132kV PK Bari(ISTS)-PK Bari, 132kV Surajmaningar(ISTS)-Surajmaningar, 132kV Surajmaningar(ISTS)- Budhjungnagar line must be in service. Intimation to NLDC
135 | OCC_241 | POWERGRID | 132KV/33KV TEZU-ICT-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 11/Sep/2026 | 09:00 | 11/Sep/2026 | 13:00 |  | SD may be availed subject to the availability of 132KV/33KV TEZU-ICT-1. Consent from AP
136 | OCC_241 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation Clearance | 11/Sep/2026 | 09:00 | 11/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
137 | OCC_241 | POWERGRID | 132KV-HAFLONG-HAFLONG-1 | D | 1. GIS Warranty Test of CB (CB Timing, DCRM and CRM). 2. LA IR. | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 15:00 |  | SD may be availed. Consent from Assam is required
138 | OCC_241 | POWERGRID | 132KV-AIZWAL-LONGMOL-1 | D | 1. GIS Warranty Testing (CB timing, CB DCRM, DC CRM), SF6 Gas Quality Analysing. 2. Relay Testing (Main and backup). 2. Luangmual Bay LA stressed conductor dropper replacement work. 3. LA IR. 4. SF6 to Air Bushing IR. | 11/Sep/2026 | 7:00 | 11/Sep/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Melriat-Aizawl line, 132kV Kumarghat-Aizawl line, 132kV Badarpur-Kolasib-Aizawl link. The connectivity during shutdown of 132kV Aizawl PG-Luangmual TL are as follows: 1) Melriat PG-Sihhmui-Luangmual-Zuangtui Old 2) Luangmual-Melriat Mz-Khawiva(Lunglei)-Kawmzawl 3) Melriat PG-Zuangtui New-Bukpui(Serchhip)-E.Lugdar 4) Melriat PG-Saitual-Vankal-Khawzawl-Champhai Note: Th SD is arpproved subjected to approval of FTC of Sihhmui-Luangmual-Zuangtui Old.
139 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
140 | OCC_241 | POWERGRID | 132KV-PASIGHAT-ROING-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations.Loc. 233,268,282,290,293,300,327 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting.S | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat link, Tinsukia-Rupai-Chapakhowa-Roing-Tezu-Namsai-Kathalguri link | SD deferred
141 | OCC_241 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | D | To check the hardware cum jungle clearance at Tower - (120 -121) | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
142 | OCC_241 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | D | To check the hardware cum jungle clearance at Tower - (120 -121) | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
143 | OCC_241 | AEGCL | 220KV-AZARA-SARUSAJAI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 403 TO 358 | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 16:00 | AGM SSJI | The SD may be availed subject to availabity of 220 kV Mirza-Sarusajai I & Azara-Sarusajai-Sonapur/J Nagar-Samaguri link., 220kV Balipara - Sonabil D/C and 220kV Misa - Samaguri D/C
144 | OCC_241 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 11/Sep/2026 | 08:00 | 11/Sep/2026 | 16:00 | AGM MNI | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
145 | OCC_241 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | C | Tower Diversion works | 12/Sep/2026 | 10:30 | 13/Sep/2026 | 18:30 | Tower Diversion works | Shutdown may be availed subject to availability of 132kV Loktak - Imphal and 132kV Loktak - Ningthoukhong line. SPS at Loktak related to tripping of one unit in case of outage two lines evacuation from Loktak(excl. 132kV Loktak - Rengpang) to be kept in ON condition during the shutdown period. Consent from NHPC is required | SD may be availed with Loktak R&M switchyard SD
146 | OCC_241 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | C | Data Shutdown Required for Tower Diversion works | 12/Sep/2026 | 10:30 | 13/Sep/2026 | 18:30 | Data Shutdown Required for Tower Diversion works | Alternate path: Loktak - Imphal - ULDC Network. | SD may be availed with Loktak R&M switchyard SD | Alternative route of data required need SCADA team input
147 | OCC_241 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.82,102,124,126,127,129 BY NIRJULI TLM | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Intimation to Assam
148 | OCC_241 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 | Bus Section I | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link,132kV Monarchak-Rabindranagar-Belonia-Bekofa-Udaipur-Palatana link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
149 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 | Bus Section I | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link,132kV Monarchak-Rabindranagar-Belonia-Bekofa-Udaipur-Palatana link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
150 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 | Bus Section I | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link,132kV Monarchak-Rabindranagar-Belonia-Bekofa-Udaipur-Palatana link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
151 | OCC_241 | POWERGRID | SILCHAR - 132KV - BUS 1 | D | AMP OF BAY EQUIPMENTS OF BUS COUPLER BAY | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 17:00 |  | SSD may be availed subject to no outage of elements. All the elements to be transferred to other bus before availing the shutdown. 132kV Aizwal - Melriat line to be in service.
152 | OCC_241 | POWERGRID | MAIN BAY () OF 132KV-TEZU-HALAIPANI-1 @TEZU - 132KV | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 13:00 | HALAIPANI BAY AT TEZU IS IDEAL CHARGED | SD may be availed
153 | OCC_241 | POWERGRID | BUS COUPLER BAY () OF SILCHAR - 132KV - BUS 1 AND SILCHAR - 132KV - BUS 2 @SILCHAR - 132KV | D | AMP OF BAY EQUPMENTS | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 17:00 |  | Sd may be availed subject to no outage of elements
154 | OCC_241 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 266 by Kolasib TLM. | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat 2 and 132kV Aizawl-Melriat line
155 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
156 | OCC_241 | MEPTCL | AMPATI - 132KV - BUS 1 | D | Preventive maintenance Work of 132 & 33 KV terminal equipments | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 12:00 | Avail | SD may be availed subject to availability of 132kV Agia-Hatsingimari line, Intimation to Assam.
157 | OCC_241 | MEPTCL | AMPATI - 132KV - BUS 2 | D | Preventive maintenance Work of 132 & 33 KV terminal equipments | 12/Sep/2026 | 08:00 | 12/Sep/2026 | 12:00 | Avail | SD may be availed subject to availability of 132kV Agia-Hatsingimari line, Intimation to Assam.
158 | OCC_241 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | D | LINE ISOLATOR ADJUSTMENT WORK | 12/Sep/2026 | 07:00 | 12/Sep/2026 | 12:00 | RE LEDO | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai and kathalguri-Namsai-Tezu-Roing-Chapakhow-Rupai link
159 | OCC_241 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.82,102,124,126,127,129 BY NIRJULI TLM | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. Intimation to Assam
160 | OCC_241 | TSECL | P K BARI - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Hailakandi-Dullavcherra-Dharmanagar link, 132kV Agtccpp-Kumarghat line, 132kV Agartala-AGTCCPP D/C, 132kV Agartala-Mohanpur-Dhalabil-Kamalpur link, Agaratala-Suramaningar-Surajmaninagar(ISTS)-PK bari-Silchar link. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period.
161 | OCC_241 | TSECL | 132KV-AGTCCPP-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
162 | OCC_241 | TSECL | 132KV-AGTCCPP-P K BARI-2 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
163 | OCC_241 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
164 | OCC_241 | TSECL | 132KV-KAILASOHAR-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
165 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
166 | OCC_241 | TSECL | 132KV-KAMALPUR-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 09:00 | 13/Sep/2026 | 16:00
167 | OCC_241 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 13/Sep/2026 | 9:00 | 13/Sep/2026 | 16:00
168 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 13/Sep/2026 | 08:00 | 13/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode
169 | OCC_241 | AEGCL | 220KV-BONGAIGAON-BTPS-2 | D | CORRIDOR CLEANING & MAINTENANCE | 14/Sep/2026 | 11:00 | 14/Sep/2026 | 13:00 | AGM SALAKATI | SD may be availed subject to availability of 220 kV BTPS-Salakati D/C and 220kV BTPS-BgTPP line-1. Combined loading of 220kV BTPS-Salakati D/C and 220kV BTPS-BgTPP line-1 to be kept within 540 MW. Intimation to NERTS
170 | OCC_241 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work 2026 | 14/Sep/2026 | 09:00 | 14/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. Intimation to Indigrid
171 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Pasighat-Roing line
172 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 55,59,101,11 by Nirjuli TLM. | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and may be be taken in Lean demand period.
173 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required. | SD deferred due to SD of 132kV Pasighat-Roing line
174 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-2 (63 MVAR) L/R@ BALIPARA - 400KV | C | OFFLINE FILTARTION OF LINE REACTOR TO MINIMISE PPM VALUE | 14/Sep/2026 | 08:00 | 19/Sep/2026 | 16:00 |  | SD may be availed
175 | OCC_241 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-2 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-3 of Mokokchung to maintained below 40 MW.
176 | OCC_241 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 307 TO 245 | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 16:00 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line.
177 | OCC_241 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
178 | OCC_241 | AEGCL | 220KV-BONGAIGAON-BTPS-1 | D | CORRIDOR CLEANING & MAINTENANCE | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 11:00 | AGM SALAKATI | SD may be availed subject to availability of 220 kV BTPS-Salakati D/C and 220kV BTPS-BgTPP line-1. Combined loading of 220kV BTPS-Salakati D/C and 220kV BTPS-BgTPP line-1 to be kept within 540 MW. Intimation to NERTS
179 | OCC_241 | AEGCL | 132KV-GOHPUR-NIRJULI-1 | C | SHIFTING OF 132kV AIS BAYS TO GIS BAYS | 14/Sep/2026 | 08:00 | 02/Oct/2026 | 16:00 | RE GHP | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. FTC required before final charging Intimation to Nerts.
180 | OCC_241 | AEGCL | BTPS - 220KV - BUS 1 | D | bus isolator maintenance & routine maintenance | 14/Sep/2026 | 08:00 | 14/Sep/2026 | 13:00 | AGM SALAKATI | SD may be availed subject to no outage of elements.
181 | OCC_241 | POWERGRID | 132KV-AGTCCPP-KUMARGHAT-1 | C | Tower Diversion works | 21/Sep/2026 | 10:30 | 27/Sep/2026 | 18:30 | Tower Diversion works | Sd may be availed subject to the availability of Badarpur-karimganj-Kumarghat link and PK Bari-Kumarghat. Intimation to NEEPCO, FTC required before final charging.
182 | OCC_241 | POWERGRID | 132KV-AGTCCPP-KUMARGHAT-1 | C | Data Shutdown Required for Tower Diversion works | 21/Sep/2026 | 10:30 | 27/Sep/2026 | 18:30 | Data Shutdown Required for Tower Diversion works | Alternate path: AGTCCPP-PK bari-Kumarghat
183 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 15/Sep/2026 | 09:00 | 15/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
184 | OCC_241 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 15/Sep/2026 | 09:00 | 15/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
185 | OCC_241 | POWERGRID | BUS COUPLER BAY (117) OF IMPHAL(PG) AIS - 132KV - BUS 1 AND IMPHAL(PG) AIS - 132KV - BUS 2 @IMPHAL(PG) AIS - 132KV | D | AMP of bay equipment | 15/Sep/2026 | 09:00 | 15/Sep/2026 | 15:00 |  | SD may be availed subject to no outage of elements.
186 | OCC_241 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEANING LOC 1 TO 56 | 15/Sep/2026 | 09:00 | 15/Sep/2026 | 16:00 | AGM TSK | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
187 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 15/Sep/2026 | 08:00 | m | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Pasighat-Roing line
188 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 55,59,101,11 by Nirjuli TLM. | 15/Sep/2026 | 08:00 | 15/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and may be be taken in Lean hydro period.
189 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 15/Sep/2026 | 08:00 | 15/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required. | SD deferred due to SD of 132kV Pasighat-Roing line
190 | OCC_241 | POWERGRID | 220KV/132KV MOKOKCHUNG (PG)-ICT-3 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 15/Sep/2026 | 08:00 | 15/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-2 of Mokokchung to maintained below 40 MW.
191 | OCC_241 | POWERGRID | MOKOKCHUNG - 220KV B/R 1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 16/Sep/2026 | 13:00 | 16/Sep/2026 | 17:00 |  | SD may be availed
192 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 16/Sep/2026 | 09:00 | 16/Sep/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
193 | OCC_241 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 16/Sep/2026 | 09:00 | 16/Sep/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
194 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Pasighat-Roing line
195 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 55,59,101,11 by Nirjuli TLM. | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and may be taken on lean hydro period
196 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required. | SD deferred due to SD of 132kV Pasighat-Roing line
197 | OCC_241 | POWERGRID | MOKOKCHUNG - 220KV - BUS 1 | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 12:00 |  | SD may be availed subject to the availability of 200kV Bus 2
198 | OCC_241 | POWERGRID | BUS COUPLER BAY () OF MOKOKCHUNG - 220KV - BUS 1 AND MOKOKCHUNG - 220KV - BUS 2 @MOKOKCHUNG - 220KV | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 16/Sep/2026 | 08:00 | 16/Sep/2026 | 12:00 |  | SD may be availed
199 | OCC_241 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 113 to 111 | 17/Sep/2026 | 10:00 | 17/Sep/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
200 | OCC_241 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 17/Sep/2026 | 09:00 | 17/Sep/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
201 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Pasighat-Roing line
202 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.60,64,101,116,166. by Nirjuli TLM. | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and may be taken on lean hydro period
203 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 17:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required. | SD deferred due to SD of 132kV Pasighat-Roing line
204 | OCC_241 | POWERGRID | MAIN BAY (201(ZHADIMA)) OF 220KV-NEW KOHIMA-MOKOKCHUNG-1 @MOKOKCHUNG - 220KV | D | To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 12:00 | 201 KOHIMA BAY AT MOKOCHUNG IS IDEAL CHARGED. | SD may be availed
205 | OCC_241 | AEGCL | 220KV-SAMAGURI-SONABIL-1 | D | PREVENTIVE MAINTENANCE LOC 1 TO 75 | 17/Sep/2026 | 08:00 | 17/Sep/2026 | 16:00 | AGM NGN T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 2, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
206 | OCC_241 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work 2026 | 18/Sep/2026 | 09:00 | 18/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. Intimation to Indigrid
207 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 18/Sep/2026 | 7:00 | 18/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
208 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.60,64,101,116,166. by Nirjuli TLM. | 18/Sep/2026 | 08:00 | 18/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and SD may be availed during lean hydro period.
209 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 18/Sep/2026 | 7:00 | 18/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
210 | OCC_241 | AEGCL | 220KV-SAMAGURI-SONABIL-2 | D | PREVENTIVE MAINTENANCE LOC 90 TO 143 | 18/Sep/2026 | 08:00 | 18/Sep/2026 | 16:00 | AGM NGN T&T | SD may be availed subject to availability of 220kV Samaguri-Sonabil Ckt 1, 220kV Misa-Samaguri D/C, 220kV Balipara - Sonabil D/C and 220kV Samaguri - Mariani (AS)
211 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-MOHANPUR-1 | D | Pre-Puja Maintenance Work 2026 | 19/Sep/2026 | 09:00 | 19/Sep/2026 | 16:00 | Bus Section II | SD may be availed subject to the availability of 132kV PK Bari-Kamalpur-Dhalabil-Mohanpur link
212 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-AGTCCPP-1 | D | Pre-Puja Maintenance Work 2026 | 19/Sep/2026 | 09:00 | 19/Sep/2026 | 16:00 | Bus Section II | SD may be availed subject to the availabitiy of 132kV Agartala-AGTCCPP-2, 132kV AGTCPP-PK Bari D/C. Intimation to NEEPCO
213 | OCC_241 | TSECL | AGARTALA (79 TILLA) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 19/Sep/2026 | 09:00 | 19/Sep/2026 | 16:00 | Bus Section II (While disconnecting bus section II, the breakers of 132kV Rokhia – Agartala Line I and II of section I will need to be opened at Agartala Grid. After isolating of Bus Section II, both the lines of Bus Section I will be reconnected to the circuit.) | Sd may be availed subject to the availability of Rokhia-Monarchak-Udaipur link, 132kV Agartal RC nagar-Pk bari D/C, 132kV Agartal RC nagar- Kumarghat link, 132kV Pk bari-Kamalpur-Dhalabil-Mohanpur link
214 | OCC_241 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | CORRIDOR CLEANING | 19/Sep/2026 | 09:00 | 19/Sep/2026 | 16:00 | AGM GOALPARA | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
215 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 19/Sep/2026 | 7:00 | 19/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
216 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.60,64,101,116,166. by Nirjuli TLM. | 19/Sep/2026 | 08:00 | 19/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and SD may be availed during lean hydro period.
217 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 19/Sep/2026 | 7:00 | 19/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
218 | OCC_241 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE BETWEEN LOC 237 TO 162 | 19/Sep/2026 | 07:00 | 19/Sep/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
219 | OCC_241 | TSECL | MANU - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 20/Sep/2026 | 09:00 | 20/Sep/2026 | 16:00 |  | SD may be availed
220 | OCC_241 | TSECL | 132KV-AMBASA-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 20/Sep/2026 | 09:00 | 20/Sep/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
221 | OCC_241 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 20/Sep/2026 | 09:00 | 20/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
222 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Pre-Puja Maintenance Work 2026 | 20/Sep/2026 | 09:00 | 20/Sep/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
223 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 20/Sep/2026 | 09:00 | 20/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
224 | OCC_241 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.60,64,101,116,166. by Nirjuli TLM. | 20/Sep/2026 | 08:00 | 20/Sep/2026 | 17:30 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli-Gohpur-BNC(PG) link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Consent from NEEPCO | SD deferred and SD may be availed during lean hydro period.
225 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 20/Sep/2026 | 7:00 | 20/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
226 | OCC_241 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 3,6,9,18 by BALIPARA TLM. | 21/Sep/2026 | 09:00 | 21/Sep/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | SD deferred and SD may be availed during lean Demand period.
227 | OCC_241 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 21/Sep/2026 | 09:00 | 21/Sep/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link.
228 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work 2026 | 21/Sep/2026 | 09:00 | 21/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
229 | OCC_241 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.65-66 by Silchar TLM. | 21/Sep/2026 | 7:00 | 21/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-2 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
230 | OCC_241 | POWERGRID | 132KV-AGTCCPP-KUMARGHAT-1 | C | For erection, de-stringing & stringing at Loc 289 of 132 KV Kumarghat RC Nagar Ckt for vulnerable tower diversion works. | 21/Sep/2026 | 08:00 | 27/Sep/2026 | 17:00 |  | Sd may be availed subject to the availability of Badarpur-karimganj-Kumarghat link and PK Bari-Kumarghat. Intimation to NEEPCO
231 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 21/Sep/2026 | 7:00 | 21/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
232 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 21/Sep/2026 | 08:00 | 21/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link | SD deferred due to SD of 132kV Tezu-Namsai
233 | OCC_241 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 89,104,138,196,200,222,241& 311) by NAMSAI TLM & Loc. 11,14,16,37,45,48, 53,57,69,73 by Tezu TLM. | 21/Sep/2026 | 7:00 | 21/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
234 | OCC_241 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 3,6,9,18 by BALIPARA TLM. | 22/Sep/2026 | 09:00 | 22/Sep/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | SD deferred and SD may be availed during lean demand period.
235 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work 2026 | 22/Sep/2026 | 09:00 | 22/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
236 | OCC_241 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 22/Sep/2026 | 09:00 | 22/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
237 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 22/Sep/2026 | 08:00 | 22/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Roing-Tezu
238 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 22/Sep/2026 | 08:00 | 22/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
239 | OCC_241 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Disc changing & jumper repairing at T/Loc-239-249 | 22/Sep/2026 | 08:00 | 22/Sep/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link.Intimation to Assam
240 | OCC_241 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc.65-66 by Silchar TLM. | 23/Sep/2026 | 09:00 | 23/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 400kV Silchar - Imphal Ckt-1 and 400kV New- Kohima - Imphal D/C. 125 MVAR BR at Imphal to be kept in open condition during the shutdown period.
241 | OCC_241 | POWERGRID | 220KV-BALIPARA-SONABIL-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 3,6,9,18 by BALIPARA TLM. | 23/Sep/2026 | 09:00 | 23/Sep/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 2, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | SD deferred and SD may be availed during lean demand period.
242 | OCC_241 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 23/Sep/2026 | 09:00 | 23/Sep/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
243 | OCC_241 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 23/Sep/2026 | 09:00 | 23/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
244 | OCC_241 | TSECL | 132KV-AMBASA-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 23/Sep/2026 | 09:00 | 23/Sep/2026 | 16:00 |  | SD may be availed. Currently, 132kV P K Bari – Manu is under outage condition, during shutdown of 132kV Ambasa – Manu, Manu S/S will be blackout.
245 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 23/Sep/2026 | 08:00 | 23/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Roing-Tezu
246 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 23/Sep/2026 | 08:00 | 23/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
247 | OCC_241 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 23/Sep/2026 | 08:00 | 23/Sep/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
248 | OCC_241 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 209-307 | 23/Sep/2026 | 08:00 | 23/Sep/2026 | 16:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
249 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 24/Sep/2026 | 09:00 | 24/Sep/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV SM Nagar-Bodhjunagar-SM Nagar(TE) link
250 | OCC_241 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 24/Sep/2026 | 09:00 | 24/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
251 | OCC_241 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING LOC 79 TO 112 | 24/Sep/2026 | 09:00 | 24/Sep/2026 | 16:00 | AGM TSK | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
252 | OCC_241 | AEGCL | 220KV-AGIA-BTPS-1 | D | CORRIDOR CLEANING | 20/Sep/2026 | 7:00 | 20/Sep/2026 | 14:00 | AGM GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high
253 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 24/Sep/2026 | 08:00 | 24/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Roing-Tezu
254 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 24/Sep/2026 | 08:00 | 24/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
255 | OCC_241 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc.5 & 22 by BALIPARA TLM | 24/Sep/2026 | 08:00 | 24/Sep/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | SD deferred and SD may be availed during lean demand period.
256 | OCC_241 | POWERGRID | 132KV/33KV NAMSAI-ICT-1 | D | 1. BUSHING TAN-DELTA & CAP 2. CT TAN-DELTA & CAP 3. LA IR 4. ISOLATOR & CB CRM 5. WTI & OTI CALIBRATION CHECKS 6. INSTALLATION OF CUSTOMISED LUGS IN EACH PHASE LV-N BUSHING AS PERMANENT SOLUTION TO HOTSPOT AND PREPARATORY MEASURE BEFORE UPCOMING FESTIVE SEASON. | 24/Sep/2026 | 07:00 | 24/Sep/2026 | 18:00 |  | SD may be availed subject to availability of other ICT. Consent from AP
257 | OCC_241 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work 2026 | 25/Sep/2026 | 09:00 | 25/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 180 MW during the SD period. Intimation to Indigrid
258 | OCC_241 | POWERGRID | MAIN BAY () OF 400KV/132KV IMPHAL(PG)-ICT-2 @IMPHAL(PG) - 400KV | D | AMP of bay equipment | 25/Sep/2026 | 09:00 | 25/Sep/2026 | 15:00 |  | SD may be availed subject to no outage of element
259 | OCC_241 | AEGCL | 220KV-AGIA-BOKO-1 | D | CORRIDOR CLEANING | 25/Sep/2026 | 09:00 | 25/Sep/2026 | 16:00 | AGM GOALPARA | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
260 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 25/Sep/2026 | 08:00 | 25/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Roing-Tezu
261 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 25/Sep/2026 | 08:00 | 25/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
262 | OCC_241 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 151-152 by Silchar TLM. | 25/Sep/2026 | 7:00 | 25/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Consent from Mizoram
263 | OCC_241 | POWERGRID | 220KV-BALIPARA-SONABIL-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc.5 & 22 by BALIPARA TLM | 25/Sep/2026 | 08:00 | 25/Sep/2026 | 16:00 |  | Sd may be availed subject to the availability of 220kV balipara-Sonabil 1, 220 kV Misa-Samaguri D/C, 400kV Mirza-Bongaigaon, BTPS-Agia D/C. Consent from Assam | SD deferred and SD may be availed during lean demand period.
264 | OCC_241 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 25/Sep/2026 | 08:00 | 25/Sep/2026 | 16:00 | AGM MNI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
265 | OCC_241 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | CORRIDOR CLEANING & MAINTENANCE | 25/Sep/2026 | 08:00 | 25/Sep/2026 | 16:00 | AGM SALAKATI | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
266 | OCC_241 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 26/Sep/2026 | 09:00 | 26/Sep/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
267 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
268 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
269 | OCC_241 | TSECL | ROKHIA - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Monarchak - Udaipur and 132kV Udaipur - Palatana. SPS at Monarchak need to be kept in off condition before availing shutdown.
270 | OCC_241 | TSECL | ROKHIA - UNIT 9 | D | Pre-Puja Maintenance Work 2026 | 12/Sep/2026 | 09:00 | 12/Sep/2026 | 16:00 |  | Sd may availed
271 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 26/Sep/2026 | 08:00 | 26/Sep/2026 | 18:00 |  | A/R may be kept in Non-Auto mode | SD deferred due to SD of 132kV Roing-Tezu
272 | OCC_241 | POWERGRID | 132KV-ROING-TEZU-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations. Loc. 111,114, 126, 139,169,192, 200,212, 216,243 by Tezu TLM Loc. 2,9,30,61,103 by Roing TLM To finalise the SAS upgradation work viz. validation with RLDC for proper signal reporting. | 26/Sep/2026 | 08:00 | 26/Sep/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
273 | OCC_241 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 151-152 by Silchar TLM. | 26/Sep/2026 | 08:00 | 26/Sep/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Kumarghat-Aizawl-Kolasib link. Consent from Mizoram
274 | OCC_241 | POWERGRID | KUMARGHAT - 132KV B/R 1 | C | Dry out & Vacuuming of 132 KV & 20 MVAR Bus Reactor at Kumarghat S/S as per instruction from RHQ,AM vide instruction from latest DGA meeting. | 26/Sep/2026 | 08:00 | 30/Sep/2026 | 23:59 |  | Shutdown may be availed
275 | OCC_241 | POWERGRID | 132KV/33KV NAMSAI-ICT-2 | D | 1. BUSHING TAN-DELTA & CAP 2. CT TAN-DELTA & CAP 3. LA IR 4. ISOLATOR & CB CRM 5. WTI & OTI CALIBRATION CHECKS 6. INSTALLATION OF CUSTOMISED LUGS IN EACH PHASE LV-N BUSHING AS PERMANENT SOLUTION TO HOTSPOT AND PREPARATORY MEASURE BEFORE UPCOMING FESTIVE SEASON. | 26/Sep/2026 | 07:00 | 26/Sep/2026 | 18:00 |  | SD may be availed subject to availability of other ICT. Consent from AP
276 | OCC_241 | TSECL | UDAIPUR (BANDUAR) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 27/Sep/2026 | 09:00 | 27/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
277 | OCC_241 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 27/Sep/2026 | 09:00 | 27/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
278 | OCC_241 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 27/Sep/2026 | 09:00 | 27/Sep/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
279 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 27/Sep/2026 | 7:00 | 27/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
280 | OCC_241 | TSECL | SURAJMANI NAGAR - 132KV - BUS 2 | D | Pre-Puja Maintenance Work 2026 | 28/Sep/2026 | 09:00 | 28/Sep/2026 | 16:00 |  | Sd may be availed subject to no outage of elements. All element shifted to Main Bus 1 online before taking SD. 132kV PK Bari(ISTS)-PK Bari, 132kV Surajmaningar(ISTS)-Surajmaningar, 132kV Surajmaningar(ISTS)- Budhjungnagar line must be in service. Intiamtion to NLDC
281 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 28/Sep/2026 | 09:00 | 28/Sep/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
282 | OCC_241 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 28/Sep/2026 | 09:00 | 28/Sep/2026 | 16:00 |  | SD may be availed
283 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 28/Sep/2026 | 7:00 | 28/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
284 | OCC_241 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 74 TO 35 | 28/Sep/2026 | 08:00 | 28/Sep/2026 | 16:00 | AGM SSJI | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
285 | OCC_241 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 29/Sep/2026 | 09:00 | 29/Sep/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. . Intimation to INDIGRID
286 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 29/Sep/2026 | 7:00 | 29/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode
287 | OCC_241 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | CORRIDOR CLEANING LOC 209 TO 238 | 29/Sep/2026 | 08:00 | 29/Sep/2026 | 16:00 | AGM GOALPARA & AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
288 | OCC_241 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | CORRIDOR CLEANING & MAINTENANCE | 29/Sep/2026 | 08:00 | 29/Sep/2026 | 16:00 | AGM SALAKATI | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
289 | OCC_241 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING LOC 237 TO 162 | 29/Sep/2026 | 07:00 | 29/Sep/2026 | 16:00 | AGM SMG & AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
290 | OCC_241 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Pre-Puja Maintenance Work 2026 | 30/Sep/2026 | 09:00 | 30/Sep/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
291 | OCC_241 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 30/Sep/2026 | 09:00 | 30/Sep/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link
292 | OCC_241 | NETCL | 400KV-BONGAIGAON-BYRNIHAT (KILLING) | D | Replacement of damaged insulators, Tightening of loose Jumper Cone N&B, Replacement of rusted Jumper Cone N&B etc. | 30/Sep/2026 | 09:00 | 30/Sep/2026 | 15:00 | Put up for OCCM approval. | S/D may be availed subject to availability of 400 kV Bongaigaon – Azara, 400 kV Silchar – Killing, 400 kV Silchar – Azara, 220 kV Agia – BTPS D/C, 220 kV Balipara – Sonabil – Samaguri D/C. The combined loading of the 220 kV BTPS–Agia D/C line should be maintained below 240 MW during the shutdown period to ensure safe and reliable operation. ATC/TTC needs to be revised. | SD deferred and SD May be availed in Nov, Dec
293 | OCC_241 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 30/Sep/2026 | 09:00 | 30/Sep/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
294 | OCC_241 | AEGCL | 220KV-AGIA-BTPS-2 | D | CORRIDOR CLEANING | 27/Sep/2026 | 7:00 | 27/Sep/2026 | 14:00 | AGM GOALPARA & AGM SALAKATI | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
295 | OCC_241 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. SHUTDOWN NOT REQUIRED. | 30/Sep/2026 | 7:00 | 30/Sep/2026 | 16:00 |  | A/R may be kept in Non-Auto mode