## Sheet1
Sl no. | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Study Comments | Remarks
1 | OCC_242 | POWERGRID | FILTER BANK 3 SUB BANK 1 at BNC | D | AMP | 01/Oct/2026 | 09:00 | 01/Oct/2026 | 17:00 |  | SD may be availed. NLDC consent is required.
2 | OCC_242 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 01/Oct/2026 | 09:00 | 01/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
3 | OCC_242 | POWERGRID | 132KV-SILCHAR-SRIKONA-1 | D | AMP (CB, CT, ISO) & RELAY TESTING WORK AT AEGCL END. | 02/Oct/2026 | 09:00 | 02/Oct/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Srikona-Pailapool line
4 | OCC_242 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 01/Oct/2026 | 09:00 | 01/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS), 132kV Surajmaninagar(ISTS)-Budhjungnagar and 132kV PKbari-Manu-Ambassa-Gamaitila-Barmura-Jiranaia-Budhjungnagar link. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
5 | OCC_242 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 01/Oct/2026 | 09:00 | 01/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Palatana-Udaipur, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line.
6 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 101-149 &1-34 | 01/Oct/2026 | 08:00 | 01/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare - North Lakimpur & Nirjuli - North Lakimpur line..
7 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 01/Oct/2026 | 08:00 | 01/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
8 | OCC_242 | POWERGRID | AIZWAL - 132KV - BUS 1 | D | WARRANTY TESTING IN GIS BUS COUPLER BAY AND BUS-1: 1. CB DCRM, CB TIMING, CB CRM. 2. SF6 QUALITY ANALYSING. | 01/Oct/2026 | 08:00 | 01/Oct/2026 | 16:00 |  | 132kV Silchar-Melriat D/C to be in service, All bus elements to remain in service via other bus, N-1 contigency of other bus can lead to blackout of 132kV Lungmual & radially connected SS of Mizoram. Consent required from Mizoram.
9 | OCC_242 | POWERGRID | AIZWAL - 132KV - BUS 1 | D | WARRANTY TESTING IN GIS BUS COUPLER BAY AND BUS-1: 1. CB DCRM, CB TIMING, CB CRM. 2. SF6 QUALITY ANALYSING. | 01/Oct/2026 | 08:00 | 01/Oct/2026 | 17:00 |  | SD may be deferred as the same is punch twice
10 | OCC_242 | POWERGRID | BUS COUPLER BAY () OF AIZWAL - 132KV - BUS 2 AND AIZWAL - 132KV - BUS 1 @AIZWAL - 132KV | D | WARRANTY TESTING IN GIS BUS COUPLER BAY AND BUS-1: 1. CB DCRM, CB TIMING, CB CRM. 2. SF6 QUALITY ANALYSING. | 01/Oct/2026 | 08:00 | 01/Oct/2026 | 17:00 |  | SD may be availed
11 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 01/Oct/2026 | 07:00 | 01/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode, 132kV Panyor to Pasighat link to be in service.
12 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 01/Oct/2026 | 07:00 | 01/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
13 | OCC_242 | POWERGRID | KUMARGHAT - 132KV B/R 1 | C | Dry out & Vacuuming of 132 KV & 20 MVAR Bus Reactor at Kumarghat S/S as per instruction from RHQ,AM vide instruction from latest DGA meeting. | 01/Oct/2026 | 00:00 | 06/Oct/2026 | 18:00 |  | Shutdown may be availed
14 | OCC_242 | NAGALAND | 132KV-KOHIMA-KARONG-1 | D | Vegetation Clearance | 02/Oct/2026 | 09:00 | 02/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Doyang-Sanis-Wokha-Chiephozou-Zhadima-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Karong-Gamphazol-Yurebam link. Manipur Consent required.
15 | OCC_242 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 02/Oct/2026 | 09:00 | 02/Oct/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link.
16 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 02/Oct/2026 | 08:00 | 02/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
17 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 02/Oct/2026 | 07:00 | 02/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
18 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 02/Oct/2026 | 07:00 | 02/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
19 | OCC_242 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 03/Oct/2026 | 09:00 | 03/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line.
20 | OCC_242 | NAGALAND | 132KV-KOHIMA-KARONG-1 | D | Vegetation Clearance | 03/Oct/2026 | 09:00 | 03/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Doyang-Sanis-Wokha-Chiephozou-Zhadima-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Karong-Gamphazol-Yurebam link. Manipur Consent required.
21 | OCC_242 | POWERGRID | 400 KV PALATANA 2 MAIN BAY(WITH 50 MVAR LINE REACTOR) (409) AT SILCHAR | D | AMP | 03/Oct/2026 | 09:00 | 03/Oct/2026 | 17:00 | ONLY MAIN BAY SHUTDOWN REQUIRED, LINE REACTOR SHUTDOWN NOT REQUIRED | SD may be availed line to remain in service via Tie-Bay.
22 | OCC_242 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 03/Oct/2026 | 09:00 | 03/Oct/2026 | 16:00 | 132kV Rokhia - Monarchak - Udaipur Line (12.4km D/C) | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
23 | OCC_242 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 03/Oct/2026 | 09:00 | 03/Oct/2026 | 16:00 | 132kV Rokhia - Monarchak - Udaipur Line (12.4km D/C) | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
24 | OCC_242 | AEGCL | 220KV-AZARA-BOKO-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 228-307 | 03/Oct/2026 | 08:30 | 03/Oct/2026 | 16:30 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
25 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 03/Oct/2026 | 08:00 | 03/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
26 | OCC_242 | POWERGRID | AIZWAL - 132KV - BUS 2 | D | WARRANTY TESTING IN GIS BUS-2: 1. SF6 QUALITY ANALYSING. | 03/Oct/2026 | 08:00 | 03/Oct/2026 | 16:00 |  | 132kV Silchar-Melriat D/C to be in service, All bus elements to remain in service via other bus, N-1 contigency of other bus can lead to blackout of 132kV Lungmual & radially connected SS of Mizoram. Consent required from Mizoram.
27 | OCC_242 | POWERGRID | AIZWAL - 132KV - BUS 2 | D | WARRANTY TESTING IN GIS BUS-2: 1. SF6 QUALITY ANALYSING. | 03/Oct/2026 | 08:00 | 03/Oct/2026 | 16:00 |  | SD may be deferred as the same is punch twice
28 | OCC_242 | POWERGRID | BUS COUPLER BAY () OF AIZWAL - 132KV - BUS 2 AND AIZWAL - 132KV - BUS 1 @AIZWAL - 132KV | D | WARRANTY TESTING IN GIS BUS-2: 1. SF6 QUALITY ANALYSING | 03/Oct/2026 | 08:00 | 03/Oct/2026 | 16:00 |  | SD may be availed.
29 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 03/Oct/2026 | 07:00 | 03/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
30 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 03/Oct/2026 | 07:00 | 03/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
31 | OCC_242 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 04/Oct/2026 | 09:00 | 04/Oct/2026 | 16:00 | 132kV Dharmanagar Bus | SD may be availed subject to availability of Hailakandi-Dullavcherra line. Intimation to Assam
32 | OCC_242 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work 2026 | 04/Oct/2026 | 09:00 | 04/Oct/2026 | 16:00 | 132kV Dharmanagar Bus | SD may be availed subject to availability of Hailakandi-Dullavcherra line. Intimation to Assam
33 | OCC_242 | TSECL | DHARMANAGAR (MISSION TILLA) - 132KV - BUS 1 | D | Pre-Puja Maintenance Work 2026 | 04/Oct/2026 | 09:00 | 04/Oct/2026 | 16:00 | 132kV Dharmanagar Bus | SD may be availed subject to availability of Hailakandi-Dullavcherra line. Intimation to Assam
34 | OCC_242 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-2 | D | Pre-Puja Maintenance Work 2026 | 04/Oct/2026 | 09:00 | 04/Oct/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 1
35 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 04/Oct/2026 | 08:00 | 04/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
36 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 04/Oct/2026 | 07:00 | 04/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
37 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 04/Oct/2026 | 07:00 | 04/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
38 | OCC_242 | AEGCL | PAILAPPOL - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 04/Oct/2026 | 05:00 | 04/Oct/2026 | 09:00 | RE PLP | Shutdown may be availed all elements to be in service via Bus-2. |  | As per our SCADA SLD Pailapool has double main bus scheme.
39 | OCC_242 | AEGCL | PAVOI - 132KV - BUS 1 | D | PREVENTICE MAINTENANCE | 04/Oct/2026 | 05:00 | 04/Oct/2026 | 09:00 | RE BNC | 132kV BNC(PG)-Gohpur and 132kV BNC(PG)-Chimpu-Gohpur link to be in service. Intimation to Nerts.
40 | OCC_242 | AEGCL | HAILAKANDI - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 05/Oct/2026 | 05:00 | 05/Oct/2026 | 14:00 | AGM PNG | SD may be availed subject to availability of 132kV Pkbari-Dharmanagar-Dullavchera
41 | OCC_242 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | C | Data Shutdown for Rectification of Lossy Span | 05/Oct/2026 | 10:30 | 05/Oct/2026 | 18:30 | Data Shutdown only required | No impact in NER communication system
42 | OCC_242 | ER-II/ERPC | 400KV-BINAGURI-BONGAIGAON-1 | D | Rectification of damaged insulators damaged due to lightning | 05/Oct/2026 | 9:00 | 05/Oct/2026 | 18:00 |  | SD may be availed, 400kV Bongaigaon-Binaguri-2, 400kV Bongaigaon-Alipurduar D/C, 220kV Salakati-Alipurduar D/C to be in service.
43 | OCC_242 | AEGCL | 132KV-TINSUKIA-MARGHERITA_AS-1 | D | CORRIDOR CLEANING FROM LOC 107-109 | 05/Oct/2026 | 10:00 | 05/Oct/2026 | 16:00 | RE LEDO | SD may be availed subject to availability of 132kV Margherita - Rupai, 132kV Tinsukai - Rupai line, 132kV Panyor-Ziro-Daporijo-Basar-Along-Pasighat-Roing link and kathalguri-Namsai-Tezu-Roing-Chapakhow-Rupai link, N-1 contignecy of 132kV Tinsukia-Rupai can lead to low voltage in Rupai and Margherita SS.
44 | OCC_242 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 05/Oct/2026 | 09:00 | 05/Oct/2026 | 16:00 | RE GLG | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
45 | OCC_242 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 05/Oct/2026 | 09:00 | 05/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
46 | OCC_242 | NAGALAND | 132KV-KOHIMA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 05/Oct/2026 | 09:00 | 05/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Wokha-Sanis-Doyang link.
47 | OCC_242 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-1 L/R@ BISWANATH CHARIALI - 400KV | D | AMP OF LINE REACTOR | 05/Oct/2026 | 09:00 | 05/Oct/2026 | 17:00 |  | Shutdown may be availed
48 | OCC_242 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 05/Oct/2026 | 09:00 | 05/Oct/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. Intimation to INDIGRID
49 | OCC_242 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 245-209 | 05/Oct/2026 | 08:30 | 05/Oct/2026 | 16:30 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line.
50 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 101-149 &1-34 | 05/Oct/2026 | 08:00 | 05/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
51 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 05/Oct/2026 | 08:00 | 05/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
52 | OCC_242 | POWERGRID | 132KV/33KV NIRJULI-ICT-1 | D | for erection of 33kV bus isolators along with necessary alignment and interconnection of jumpers/dropper to associates/adjacent bay equipment for restoration of 33kV Bay (AP-03) at Nirjuli S/S. | 05/Oct/2026 | 08:00 | 05/Oct/2026 | 19:00 |  | SD may be availed
53 | OCC_242 | NEEPCO | KHANDONG - UNIT 2 | C | 1. TGB housing oil leakage arresting. 2. Cleaning of UGB and LCB coolers. | 05/Oct/2026 | 08:00 | 06/Oct/2026 | 20:00 |  | SD may be availed. Consent of beneficiary is required.
54 | OCC_242 | Arunachal Pradesh | 132KV-PARE-ITANAGAR-2 | D | Vegetation Clearance | 28/Oct/2026 | 7:00 | 28/Oct/2026 | 14:00 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Panyor-Pare-Nirjuli-Gohpur-BNC link, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
55 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-ITANAGAR-1 | D | Vegetation Clearance | 28/Oct/2026 | 7:00 | 28/Oct/2026 | 14:00 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Panyor-Pare-Nirjuli-Gohpur-BNC link, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
56 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 05/Oct/2026 | 07:00 | 05/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
57 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 05/Oct/2026 | 07:00 | 05/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
58 | OCC_242 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | CORRIDOR CLEANING LOC 39-82 | 06/Oct/2026 | 9:00 | 06/Oct/2026 | 16:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
59 | OCC_242 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 406,452,369 by Aizawl TLM. | 06/Oct/2026 | 10:00 | 06/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
60 | OCC_242 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 1 TO 9 | 06/Oct/2026 | 09:30 | 06/Oct/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Daporizo-Basar-Along-Pasighat-Roing link. Intimation to AP and NERTS
61 | OCC_242 | AEGCL | 132KV-SRIKONA-PANCHGRAM (NEW)-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 16:00 | AGM PNG | SD may be availed
62 | OCC_242 | AEGCL | 220KV-AGIA-BTPS-1 | D | PRE PUJA PREVENTIVE MAINTENANCE | 04/Oct/2026 | 7:00 | 04/Oct/2026 | 14:00 | AGM GOAPT&T | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled.The SD will be deferred when the NER demand is high
63 | OCC_242 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripra
64 | OCC_242 | NAGALAND | 132KV-KOHIMA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Wokha-Sanis-Doyang link.
65 | OCC_242 | POWERGRID | 220KV/132KV DIMAPUR-ICT-1 | D | Warranty Test of ICT-1 | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 17:00 |  | SD may be availed subject to availability 220/132kV ICT-2 & ICT-3 at Dimapur and 132kV Dimapur – Imphal line.
66 | OCC_242 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Vegetation Clearance | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. Intimation to NERTS
67 | OCC_242 | POWERGRID | TIE BAY () OF 400KV-IMPHAL(PG)-400 KV NEW KOHIMA-1 AND 400KV/132KV IMPHAL(PG)-ICT-1 @IMPHAL(PG) - 400KV | D | AMP | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 15:00 |  | SD may be availed subject to the availability of main bay of 400kV Imphal-New Kohima-1 at Imphal-400kV & main bay of 315 MVA ICT 1 at Imphal-400kV
68 | OCC_242 | POWERGRID | 400 KV, 200 MVA ICT 2 MAIN BAY AT SILCHAR | D | AMP | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 17:00 |  | SD may be availed
69 | OCC_242 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
70 | OCC_242 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Pre-Puja Maintenance Work 2026 | 06/Oct/2026 | 09:00 | 06/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
71 | OCC_242 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
72 | OCC_242 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING LOC 314-238 | 07/Oct/2026 | 08:00 | 07/Oct/2026 | 15:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
73 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 150-198 & 35-68 | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
74 | OCC_242 | Arunachal Pradesh | 132KV-PARE-ITANAGAR-2 | D | Vegetation Clearance | 29/Oct/2026 | 7:00 | 29/Oct/2026 | 14:00 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Panyor-Pare-Nirjuli-Gohpur-BNC link, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
75 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-ITANAGAR-1 | D | Vegetation Clearance | 29/Oct/2026 | 0.29167 | 29/Oct/2026 | 0.58333 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Panyor-Pare-Nirjuli-Gohpur-BNC link, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
76 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line.
77 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
78 | OCC_242 | POWERGRID | 132KV/33KV NIRJULI-ICT-1 | D | for erection of 33kV bus isolators along with necessary alignment and interconnection of jumpers/dropper to associates/adjacent bay equipment for restoration of 33kV Bay (AP-03) at Nirjuli S/S. | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 19:00 |  | SD may be availed subject to availability of 132KV/33KV NIRJULI-ICT-1, Intimation to AP.
79 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 06/Oct/2026 | 08:00 | 06/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
80 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 06/Oct/2026 | 07:00 | 06/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | To be deferred due to Rupai-Chapakhowa SD
81 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 06/Oct/2026 | 07:00 | 06/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
82 | OCC_242 | AEGCL | AZARA - 400KV - BUS 1 | D | BUS TIGHTENING &BUS ISOLATOR ALIGNMENT & PRE PUJA ROUTINE MAINTENANCE | 06/Oct/2026 | 07:00 | 06/Oct/2026 | 16:00 | AGM MIRZA | SD may be availed subject to no outage of elements, Tie Bay of Bongaingaon Azara & 400/220kV Azara ICT-1 to be in service,220kV BTPS-Agia D/C, 220kV Agia-Chaygaon-Azara, 220kV Agia-Boko -Azara link, 220kV Samaguri-Sonapur-Sarusjai link and 220kV Samaguri-Jawaharnagar-Sarusajai link to be in service.
83 | OCC_242 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | C | Data Shutdown for Tower Diversion works | 07/Oct/2026 | 10:30 | 08/Oct/2026 | 18:30 | Data Shutdown only required | Subject to availability of Loktak - Imphal and Jiribam - Haflong. And Diversion of services via Loktak - Imphal and Jiribam - Haflong
84 | OCC_242 | POWERGRID | 132KV-AIZWAL-TIPAIMUMK-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 406,452,369 by Aizawl TLM. | 07/Oct/2026 | 10:00 | 07/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Jiribam(PG) - Tipaimukh. Consent from Manipur
85 | OCC_242 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 93 to 91. | 07/Oct/2026 | 10:00 | 07/Oct/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
86 | OCC_242 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING LOC 1 TO 108 | 07/Oct/2026 | 09:30 | 07/Oct/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link & 132 Rupai -Margarita -Tinsukia link
87 | OCC_242 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service. Intimation to NERTS
88 | OCC_242 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
89 | OCC_242 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
90 | OCC_242 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE &CORRIDOR CLEANING | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 | RE BKJ | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
91 | OCC_242 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 | AGM PNG | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
92 | OCC_242 | NAGALAND | 132KV-KOHIMA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Wokha-Sanis-Doyang link.
93 | OCC_242 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Vegetation Clearance | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. Intimation to NERTS
94 | OCC_242 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 07/Oct/2026 | 09:00 | 07/Oct/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link.
95 | OCC_242 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
96 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | C | Facilitating de-stringing & stringing works related to diversion of Section of 132 kV S/C Dimapur – Imphal TL under Imphal jurisdiction in view of shifting of endangered tower Location No. 278. | 07/Oct/2026 | 08:00 | 15/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 400/132kV ICT 1 &2 at 400kV Imphal S/S
97 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 07/Oct/2026 | 08:00 | 07/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line.
98 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 07/Oct/2026 | 08:00 | 07/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
99 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-ITANAGAR-1 | D | Vegetation Clearance | 30/Oct/2026 | 7:00 | 30/Oct/2026 | 14:00 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Pare-Nirjuli-Gohpur-BNC link, 132kV Pare-Chimpu line, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. Maximum 260 MW of Ranganadi can be scheduled during the SD period. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
100 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-PARE-1 | D | Vegetation Clearance | 30/Oct/2026 | 7:00 | 30/Oct/2026 | 14:00 | Ranganadi-Pare line 2 | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Pare-Nirjuli-Gohpur-BNC link, 132kV Pare-Chimpu line, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. Maximum 260 MW of Ranganadi can be scheduled during the SD period. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
101 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 07/Oct/2026 | 08:00 | 07/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line. Consent from Nagaland
102 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 07/Oct/2026 | 07:00 | 07/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | To be deferred.
103 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 07/Oct/2026 | 07:00 | 07/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
104 | OCC_242 | MEPTCL | KHLIEHRIAT(ME) - 132KV - BUS 1 | D | Maintenance work | 08/Oct/2026 | 10:00 | 08/Oct/2026 | 16:00 | Avail | S/D may be availed Subject to the availability of 132kV Badarpur -Panchgram-Lumshnong link, 220kV Killing-Mawngap D/C and 220/132kV ICTs at Mawngap, 132kV Killing-EPIP-1-Epip 2-Umtru, 132kV Killing-EPIP-1-Epip 2-newUmtru-Umtru-Umian III-Umiam I link, 132kv Umiam I - Umiam(loading to be mainated under 55 MW), 132kV Umiam I-Mawlai(loading to be maintained under 35 MW). Khandong -kopili-misa link needs to be present. Intimation to NERTS
105 | OCC_242 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 | AGM PNG | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
106 | OCC_242 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | D | Electromechanical Relay replacement for integration of Body protection of Transformer with Numerical Relay & Warranty Test of ICT-2 | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 17:00 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
107 | OCC_242 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Vegetation Clearance | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. Intimation to NERTS
108 | OCC_242 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation Clearance | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
109 | OCC_242 | POWERGRID | 400 KV BYRNIHAT MAIN BAY ( WITH 63 MVAR LINE REACTOR ) (403) AT SILCHAR | D | AMP | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 17:00 | ONLY MAIN BAY SHUTDOWN REQUIRED, LINE REACTOR SHUTDOWN NOT REQUIRED. BAY NO. IS 406 | SD may be availed
110 | OCC_242 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
111 | OCC_242 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Pre-Puja Maintenance Work 2026 | 08/Oct/2026 | 09:00 | 08/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link. Intimation to INDIGRID
112 | OCC_242 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 42 | 09/Oct/2026 | 08:30 | 09/Oct/2026 | 16:30 | AGM SSJI | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
113 | OCC_242 | Arunachal Pradesh | 220KV-AGBPP-DEOMALI-1 | D | Rectification of Y-B Phase | 08/Oct/2026 | 08:30 | 08/Oct/2026 | 16:00 |  | SD may be availed. Deomali and Khonsa substation will under dark. Intimation to neepco
114 | OCC_242 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 314-238 | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 16:00 | AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
115 | OCC_242 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
116 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line.
117 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
118 | OCC_242 | POWERGRID | 132KV/33KV NIRJULI-ICT-2 | D | for erection of 33kV bus isolators along with necessary alignment and interconnection of jumpers/dropper to associates/adjacent bay equipment for restoration of 33kV Bay (AP-03) at Nirjuli S/S. | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 19:00 |  | Sd may be subject to the availability of 132/33kV ICT-1. consent from AP
119 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-ITANAGAR-1 | D | Vegetation Clearance | 31/Oct/2026 | 7:00 | 31/Oct/2026 | 14:00 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Pare-Nirjuli-Gohpur-BNC link, 132kV Pare-Chimpu line, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. Maximum 260 MW of Ranganadi can be scheduled during the SD period. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
120 | OCC_242 | Arunachal Pradesh | 132KV-RANGANADI-PARE-2 | D | Vegetation Clearance | 31/Oct/2026 | 0.29167 | 31/Oct/2026 | 0.58333 |  | SD may be availed subject to the availability of 400/132kV ICTs at Panyor, 400kV BNC-Panyor D/C, 132kV Panyor-Lekhi-Chimpu-BNC link, 132kV Pare-Nirjuli-Gohpur-BNC link, 132kV Pare-Chimpu line, 400/132kV ICTs at BNC(PG). When one machine of Ranganadi is scheduled, then one machine of Pare needs to be scheduled. Also, When two machine of Ranganadi is scheduled, then two machine of Pare needs to be scheduled. Maximum 260 MW of Ranganadi can be scheduled during the SD period. During the SD period, maximum of 180 MW needs to be maintained in the Assam Gohpur and Arunachal capital area. Intimation to NEEPCO and Consent from Assam is required
121 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 08/Oct/2026 | 08:00 | 08/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-Auto mode
122 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 08/Oct/2026 | 07:00 | 08/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | To be deferred | SD deferred
123 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 08/Oct/2026 | 07:00 | 08/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
124 | OCC_242 | AEGCL | AZARA - 400KV - BUS 2 | D | BUS TIGHTENING &BUS ISOLATOR ALIGNMENT & PRE PUJA ROUTINE MAINTENANCE | 08/Oct/2026 | 07:00 | 08/Oct/2026 | 16:00 | AGM MIRZA | SD may be availed subject to no outage of elements, Tie Bay of Bongaingaon Azara & 400/220kV Azara ICT-1 to be in service,220kV BTPS-Agia D/C, 220kV Agia-Chaygaon-Azara, 220kV Agia-Boko -Azara link, 220kV Samaguri-Sonapur-Sarusjai link and 220kV Samaguri-Jawaharnagar-Sarusajai link to be in service.
125 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | C | Data Shutdown for Rectification of Lossy Span | 09/Oct/2026 | 10:30 | 10/Oct/2026 | 18:30 | Data Shutdown only required | Subject to availability of Dimapur - Kohima section. |  | Line SD req?
126 | OCC_242 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 91 TO 158 | 09/Oct/2026 | 09:30 | 09/Oct/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Daporizo-Basar-Along-Pasighat-Roing link. Intimation to AP and NERTS
127 | OCC_242 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya
128 | OCC_242 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 | RE GLG | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
129 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | D | Replacement of flashover insulators at locs 16,20,30, 42, 46 | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 |  | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-2. Intimation to NEEPCO
130 | OCC_242 | POWERGRID | 220KV/132KV DIMAPUR-ICT-2 | D | Electromechanical Relay replacement for integration of Body protection of Transformer with Numerical Relay & Warranty Test of ICT-2 | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 17:00 |  | Sd may be availed subject to the availability of 220kV/132kV Dimapur-ICt 1 and 3 and 132kV Dimapur-Imphal
131 | OCC_242 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | Vegetation Clearance | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
132 | OCC_242 | NAGALAND | 132KV-WOKHA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou link and 132kV Wokha-Sanis-Doyang link. | SD deferred due to SD of 132kV Dimapur-Kohima line
133 | OCC_242 | POWERGRID | MAIN BAY (419) OF IMPHAL(PG) - 400KV - BUS 2 FUTURE @IMPHAL(PG) - 400KV | D | AMP | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 15:00 |  | SD may be availed
134 | OCC_242 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
135 | OCC_242 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 | 132kV Rokhia - Monarchak - Udaipur Line (12.4km D/C) | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
136 | OCC_242 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Pre-Puja Maintenance Work 2026 | 09/Oct/2026 | 09:00 | 09/Oct/2026 | 16:00 | 132kV Rokhia - Monarchak - Udaipur Line (12.4km D/C) | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
137 | OCC_242 | Arunachal Pradesh | 220KV-AGBPP-DEOMALI-1 | D | Rectification of Y-B Phase | 09/Oct/2026 | 08:30 | 09/Oct/2026 | 16:00 |  | SD may be availed. Deomali and Khonsa substation will under dark. Intimation to neepco
138 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 09/Oct/2026 | 08:00 | 09/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-2 and 132kV Doyang-Mokokchung line.
139 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 09/Oct/2026 | 08:00 | 09/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
140 | OCC_242 | POWERGRID | 132KV/33KV NIRJULI-ICT-2 | D | for erection of 33kV bus isolators along with necessary alignment and interconnection of jumpers/dropper to associates/adjacent bay equipment for restoration of 33kV Bay (AP-03) at Nirjuli S/S. | 09/Oct/2026 | 08:00 | 09/Oct/2026 | 19:00 |  | Sd may be subject to availability of 132KV/33KV NIRJULI-ICT-1, consent from AP
141 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 09/Oct/2026 | 08:00 | 09/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
142 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 09/Oct/2026 | 07:00 | 09/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
143 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 09/Oct/2026 | 07:00 | 09/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
144 | OCC_242 | ER-II/ERPC | 400KV-BINAGURI-BONGAIGAON-2 | D | Rectification of damaged insulators damaged due to lightning | 10/Oct/2026 | 9:00 | 10/Oct/2026 | 18:00 |  | SD may be availed, 400kV Bongaigaon-Binaguri-1, 400kV Bongaigaon-Alipurduar D/C, 220kV Salakati-Alipurduar D/C to be in service.
145 | OCC_242 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 10/Oct/2026 | 09:00 | 10/Oct/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya
146 | OCC_242 | POWERGRID | 132KV-SILCHAR-SRIKONA-2 | D | AMP OF BAY EQUIPMENTS AND RELAY TESTING WORK AT AEGCL | 10/Oct/2026 | 09:00 | 10/Oct/2026 | 17:00 |  | SD may be availed subject to the availability of 132KV-SILCHAR-SRIKONA-1 and 132kV Jiribam-Pailapool-Srikona link.
147 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-1 | D | Replacement of flashover insulators at locs 16,20,30, 42, 46 | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-2. Intimation to NEEPCO
148 | OCC_242 | NAGALAND | 132KV-WOKHA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 10/Oct/2026 | 09:00 | 10/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou link and 132kV Wokha-Sanis-Doyang link.
149 | OCC_242 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-2 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
150 | OCC_242 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Pre-Puja Maintenance Work 2026 | 10/Oct/2026 | 09:00 | 10/Oct/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
151 | OCC_242 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Pre-Puja Maintenance Work 2026 | 10/Oct/2026 | 09:00 | 10/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS) and 132kV Surajmaninagar(ISTS)-Budhjungnagar. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
152 | OCC_242 | Arunachal Pradesh | 220KV-AGBPP-DEOMALI-1 | D | Rectification of Y-B Phase | 10/Oct/2026 | 08:30 | 10/Oct/2026 | 16:00 |  | SD may be availed. Deomali and Khonsa substation will under dark. Intimation to neepco
153 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 10/Oct/2026 | 08:00 | 10/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
154 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 10/Oct/2026 | 07:00 | 10/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
155 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 10/Oct/2026 | 07:00 | 10/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
156 | OCC_242 | AEGCL | AGIA - 220KV - BUS 1 | D | PRE PUJA MAINTENANCE | 10/Oct/2026 | 06:00 | 10/Oct/2026 | 10:00 | AGM GOAL | SD may be availed subject to availability of all elements via other BUS, 400kV Bongaingaon-Azara, 400kV Silchar-Azara, 220kV Samagur-Jawharnagar-Sarusajai and 220kV Samagur-Sonapur-Sarusajai link to be in service.
157 | OCC_242 | AEGCL | AGIA - 220KV - BUS 2 | D | PRE PUJA MAINTENANCE | 12/Oct/2026 | 5:00 | 12/Oct/2026 | 8:00 | AGM GOAL | SD may be availed subject to availability of all elements via other BUS, 400kV Bongaingaon-Azara, 400kV Silchar-Azara, 220kV Samagur-Jawharnagar-Sarusajai and 220kV Samagur-Sonapur-Sarusajai link to be in service.
158 | OCC_242 | AEGCL | 132KV-KARIMGANJ (AS)-KUMARGHAT-1 | D | PRE PUJA PREVENTIVE MAINTENANCE | 10/Oct/2026 | 05:30 | 10/Oct/2026 | 08:30 | RE KMJ | Sd may be availed . Intimation to NERTS
159 | OCC_242 | AEGCL | 132KV-BADARPUR-KARIMGANJ (AS)-1 | D | PRE PUJA PREVENTIVE MAINTENANCE | 10/Oct/2026 | 05:30 | 10/Oct/2026 | 08:30 | RE KMJ
160 | OCC_242 | AEGCL | KARIMGANJ (AS) - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 10/Oct/2026 | 05:30 | 10/Oct/2026 | 08:30 | RE KRM
161 | OCC_242 | AEGCL | RANGIA GSS - 132KV - BUS 1 | D | PREVENTICE MAINTENANCE | 10/Oct/2026 | 05:00 | 10/Oct/2026 | 10:00 | AGM RNG | SD may be availed subject to availability of 220kV BTPS-Rangia D/C line, 220kV Rangia-Amingaon D/C, 132kV Amingaon-Kamalpur-Rangia D/C link
162 | OCC_242 | NAGALAND | 132KV-WOKHA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou link and 132kV Wokha-Sanis-Doyang link.
163 | OCC_242 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 |  | SD may be availed
164 | OCC_242 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-SURAJMANI NAGAR | D | Pre-Puja Maintenance Work 2026 | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV SM Nagar(ISTS)- Budhjungnagar - SM Nagar(Tr) link, 132kV Palatana - SM Nagar and 132kV PK Bari(ISTS) - PK Bari. The combined loading of 132kV PK Bari(ISTS)-PK Bari(Tr) and 132kV SM Nagar(ISTS)-Bodhjungnagar to be maintained below 220 MW during the SD period. Intimation to Indigrid
165 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 11/Oct/2026 | 08:00 | 11/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode.
166 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 11/Oct/2026 | 07:00 | 11/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
167 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 11/Oct/2026 | 07:00 | 11/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
168 | OCC_242 | AEGCL | PANCHGRAM (OLD) - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 11/Oct/2026 | 06:00 | 11/Oct/2026 | 11:00 | AGM PNG | SD may be availed subject to availability of 132kV Khleihriat-Lumshnong line, Meghalaya consent required.
169 | OCC_242 | AEGCL | AGIA - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE | 11/Oct/2026 | 5:00 | 11/Oct/2026 | 8:00 | AGM GOAL | SD may be availed subject to availability of 132kV Mawngap - Nongstoin - Nangalbibra link, 132kV Nangalbibra-Rongkhon-Ampati-Hatsingimari link, Ganol generation to be kept 20 MW during the SD period. Consent required from Meghalaya.
170 | OCC_242 | AEGCL | DULLAVCHERRA - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 11/Oct/2026 | 05:30 | 11/Oct/2026 | 11:30 | AGM PNG | SD may be availed subject to the availability of 132kV PK Bari-Dharmanagar. Consent from Tripura
171 | OCC_242 | AEGCL | MARGHRRITA - 132KV - BUS 1 | D | PRE PUJA MAINTENANCE (MAIN BUS) | 11/Oct/2026 | 05:00 | 11/Oct/2026 | 08:00 | RE LEDO | SD may be availed 132kV Tinsukia-Rupai-Chapakhowa-Roing link to be in service.
172 | OCC_242 | POWERGRID | 220KV-MISA-KOPILI-1 | C | Data Shutdown for Rectification of Lossy Span | 12/Oct/2026 | 10:30 | 12/Oct/2026 | 18:30 | Data Shutdown only required | Subject to availability of Misa - Kopili-2 & Misa - balipara. Services diversion via Misa-Kopili-2 or Misa - balipara |  | Line SD req?
173 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | D | Dimond formation of OPGW at Loc 4273-4274 | 12/Oct/2026 | 8:00 | 12/Oct/2026 | 16:00 | Dimond formation of OPGW at Loc 4273-4274 | SD may be availed subject to availability of 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2, 400kV BNC-Balipara-Bongaingaon-Alipurduar/Binaguri link.
174 | OCC_242 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Pre-Puja Maintenance Work 2026 | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
175 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | D | Replacement of flashover insulators at locs 16,20,30, 42, 46 | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-1. Intimation to NEEPCO
176 | OCC_242 | NAGALAND | 132KV-WOKHA-CHIEPEBOZOU-1 | D | Vegetation Clearance | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou link and 132kV Wokha-Sanis-Doyang link.
177 | OCC_242 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-1 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-Auto mode
178 | OCC_242 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Pre-Puja Maintenance Work 2026 | 12/Oct/2026 | 09:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link, 132kV Monarchak-Udaipur, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line. Intimation to OTPC
179 | OCC_242 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 35 TO 25 | 12/Oct/2026 | 08:30 | 12/Oct/2026 | 16:30 | AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
180 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement to ACSR moose terminal connectors of all equipment | 12/Oct/2026 | 08:00 | 12/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period. Consent from Assam
181 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 12/Oct/2026 | 08:00 | 12/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
182 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 12/Oct/2026 | 07:00 | 12/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
183 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 12/Oct/2026 | 07:00 | 12/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
184 | OCC_242 | AEGCL | 220KV-AGIA-BOKO-1 | D | PRE PUJA PREVENTIVE MAINTENANCE | 15/Oct/2026 | 09:00 | 15/Oct/2026 | 16:00 | AGM GOAPT&T | SD may be availed subject to the availability of 400kV Bongaigaon - Mirza, 220 kV Mirza - Boko line and 220 kV Agia - Mirza line
185 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | D | For removal of E/W from 400KV D/C Fatehabad-Agra South line | 13/Oct/2026 | 13:00 | 13/Oct/2026 | 15:00 |  | SD may be availed subject to availability of 400kV BNC-Balipara-Bongaigaon link, 400kV Bongaingaon-APD D/C, 400kV Bongaingaon-New siliguri D/C, 400kV Bongaingaon-Azara line, SD should strictly return before 16:00 Hrs, Timings should be 07:00 to 15:00 Hrs for Ckt-2 and 13:00 to 15:00 Hrs for Ckt-1. SD needs to be strictly adhered to approved timing
186 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | D | Dimond formation of OPGW at Loc 4273-4274 | 13/Oct/2026 | 7:00 | 13/Oct/2026 | 15:00 |  | SD may be availed subject to availability of 400kV BNC-Balipara-Bongaigaon link, 400kV Bongaingaon-APD D/C, 400kV Bongaingaon-New siliguri D/C, 400kV Bongaingaon-Azara line, SD should strictly return before 16:00 Hrs, Timings should be 07:00 to 15:00 Hrs for Ckt-2 and 13:00 to 15:00 Hrs for Ckt-1. SD needs to be strictly adhered to approved timing
187 | OCC_242 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
188 | OCC_242 | POWERGRID | 132KV-DIMAPUR(PG)-DOYANG-2 | D | Replacement of flashover insulators at locs 16,20,30, 42, 46 | 13/Oct/2026 | 09:00 | 13/Oct/2026 | 16:00 |  | SD may be availed subjected to availability of 132KV-DIMAPUR(PG)-DOYANG-1. Intimation to NEEPCO
189 | OCC_242 | POWERGRID | TIE BAY (420) OF 400KV-IMPHAL(PG)-THOUBAL-2 AND FUTURE @IMPHAL(PG) - 400KV | D | AMP | 13/Oct/2026 | 09:00 | 13/Oct/2026 | 15:00 |  | SD may be availed
190 | OCC_242 | POWERGRID | A/R of 132KV-DIMAPUR(PG)-DOYANG-1 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 13/Oct/2026 | 09:00 | 13/Oct/2026 | 16:00 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
191 | OCC_242 | TSECL | 132KV-AGARTALA (79 TILLA)-SURAJMANI NAGAR-1 | D | Pre-Puja Maintenance Work 2026 | 13/Oct/2026 | 09:00 | 13/Oct/2026 | 16:00 |  | SD may be availed subject to the availabitiy of 132 KV Surjamaninagar - Agartala line 2
192 | OCC_242 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
193 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 199-249 & 69-100 | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
194 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement to ACSR moose terminal connectors of all equipment | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period.Consent from Assam
195 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
196 | OCC_242 | POWERGRID | MARIANI (AS) - 220KV - BUS 2 | D | 220KV POWERGRID bay's(202) Zebra Terminal Connectors replacement to ACSR moose terminal connectors of Bus side isolators. ACSR Zebra conductor replacement with ACSR moose conductor of transfer isolator to Bus portion for improved Thermal capacity as discussed in OCCM. | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 16:00 |  | SD may be availed subject to availability of all elements via other Bus, 132kV Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220kV AGBPP-Mariani line, 132kV Rupai-Chapakhowa-Roing link, 132kV Nazira-Teok line, 132kV LTPS-Nazira D/C line, 132kV LTPS-Mariani line & 132kV LTPS-NTPS line, Upper Assam load to be kept below 350 MW during SD period considering N-1 contigency of other Mariani 220kV Bus. Consent from Assam is required
197 | OCC_242 | POWERGRID | MARIANI (AS) - 220KV - BUS 2 | D | 220KV POWERGRID bay's(202) Zebra Terminal Connectors replacement to ACSR moose terminal connectors of Bus side isolators. ACSR Zebra conductor replacement with ACSR moose conductor of transfer isolator to Bus portion for improved Thermal capacity as discussed in OCCM. | 13/Oct/2026 | 08:00 | 13/Oct/2026 | 16:00 |  | SD defererd as punched twice
198 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 13/Oct/2026 | 07:00 | 13/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
199 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 13/Oct/2026 | 07:00 | 13/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
200 | OCC_242 | AEGCL | 400KV/220KV AZARA-ICT-2 | D | PRE PUJA MAINTENANCE | 01/Oct/2026 | 07:00 | 01/Oct/2026 | 15:00 | AGM MIRZA | SD may be availed sibject to availability of 400/220kV ICT 1 at Azara, 220 Agia-BTPS D/C, 220kV Bongaigaon-Salakati-BTPS D/C, 220kV Agia-Mirza, 220kV Agia-Mirza-Boko,220kV Mirza-Sarusajai-sonapur-Samaguri link
201 | OCC_242 | POWERGRID | 132KV-RANGANADI-ZIRO-1 | C | Data Shutdown for Rectification of Lossy Span | 14/Oct/2026 | 10:30 | 14/Oct/2026 | 18:30 | Data Shutdown only required | Subject to data diversion of Ziro via Ziro->Daporizo->Basar-->Along-->Pasighat-->Roing-->Tezu-->Namsai-->NERLDC Guwahati
202 | OCC_242 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | CORRIDOR CLEANING LOC 1-42 | 14/Oct/2026 | 10:00 | 14/Oct/2026 | 17:00 | AGM TSK | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
203 | OCC_242 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | CORRIDOR CLEANING FROM LOC 112-115 & 1 TO 108 | 14/Oct/2026 | 10:00 | 14/Oct/2026 | 16:00 | RE LEDO & RE RUPAI | S/D may be availed subject to the availability of 132kV Tinsukia-Rupai and 132kV Tinsukia-Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
204 | OCC_242 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 90 to 88. | 14/Oct/2026 | 10:00 | 14/Oct/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
205 | OCC_242 | AEGCL | 400KV-AZARA-BONGAIGAON-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING | 11/Oct/2026 | 09:00 | 11/Oct/2026 | 13:00 | AGM MIRZA | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon. SD may be deferred if NER demand is high in real time
206 | OCC_242 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | PRE PUJA MAINTENANCE & CORRIDOR CLEANING LOC 237-162 & 74 TO 32 | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 | AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
207 | OCC_242 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING LOC 237-162 | 15/Oct/2026 | 08:00 | 15/Oct/2026 | 15:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
208 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 150-198 & 35-68 | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
209 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement to ACSR moose terminal connectors of all equipment | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period. Consent from Assam
210 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
211 | OCC_242 | POWERGRID | MARIANI (AS) - 220KV - BUS 1 | D | 220KV POWERGRID bay's(202) existing Bus -A isolators ACSR Zebra terminal connectors replacement with ACSR moose terminal connectors for improved Thermal capacity as discussed in OCCM. | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 |  | SD may be availed subject to availability of all elements via other Bus, 132kV Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220kV AGBPP-Mariani line, 132kV Rupai-Chapakhowa-Roing link, 132kV Nazira-Teok line, 132kV LTPS-Nazira D/C line, 132kV LTPS-Mariani line & 132kV LTPS-NTPS line, Upper Assam load to be kept below 350 MW during SD period considering N-1 contigency of other Mariani 220kV Bus. Consent from Assam is required
212 | OCC_242 | POWERGRID | MARIANI (AS) - 220KV - BUS 1 | D | 220KV POWERGRID bay's(202) existing Bus -A isolators ACSR Zebra terminal connectors replacement with ACSR moose terminal connectors for improved Thermal capacity as discussed in OCCM. | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 |  | SD defererd as punched twice | SD deferred
213 | OCC_242 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Jungle clearance at Tower -60 &61 | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
214 | OCC_242 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Jungle clearance at Tower -60 &61 | 14/Oct/2026 | 08:00 | 14/Oct/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
215 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 14/Oct/2026 | 07:00 | 14/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
216 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 14/Oct/2026 | 07:00 | 14/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
217 | OCC_242 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 15/Oct/2026 | 09:00 | 15/Oct/2026 | 16:00 | RE PLP | S/D may be availed subject to 132kV Srikona-Pailapool.
218 | OCC_242 | NAGALAND | 132KV-SANIS-WOKHA-1 | D | Vegetation Clearance | 15/Oct/2026 | 09:00 | 15/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Kohima-Zhadima-Chiephobozou-Wokha-Sanis link.
219 | OCC_242 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 15/Oct/2026 | 08:00 | 15/Oct/2026 | 16:00 | AGM RNG | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
220 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 15/Oct/2026 | 08:00 | 15/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
221 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 15/Oct/2026 | 07:00 | 15/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
222 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 15/Oct/2026 | 07:00 | 15/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
223 | OCC_242 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | C | Data Shutdown for Rectification of Lossy Span | 16/Oct/2026 | 10:30 | 16/Oct/2026 | 18:30 | Data Shutdown only required | Subject to data diversion of Melriat via Melriat --> Aizawl --> NERLDC Guwahati
224 | OCC_242 | AEGCL | 132KV-AGIA-HATSINGIMARI-1 | D | PREVENTIVE MAINTENANCE &CORRIDOR CLEANING | 16/Oct/2026 | 09:00 | 16/Oct/2026 | 16:00 | AGM GOAPT&T | S/D may be availed subject to availability of 132 kV Nangalbibra - Rongkhon - Ampati - Hastingimari link. Consent from Meghalaya is required to support load of Hastingmari during the shutdown period.
225 | OCC_242 | NAGALAND | 132KV-SANIS-WOKHA-1 | D | Vegetation Clearance | 16/Oct/2026 | 09:00 | 16/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou-Wokha link and 132kV Doyang-Sanis.
226 | OCC_242 | POWERGRID | MAIN BAY (421) OF 400KV-IMPHAL(PG)-THOUBAL-2 @IMPHAL(PG) - 400KV | D | AMP | 16/Oct/2026 | 09:00 | 16/Oct/2026 | 15:00 |  | SD may be availed line to remain in service via Tie-Bay.
227 | OCC_242 | POWERGRID | 132KV-BADARPUR-KHLIEHRIAT-1 | D | REPLACEMENT OF CRTICAL CLRI STRING IN TOWER NO.153, TN 159A, TN 191, TN 195 OF 132KV S/C BADARPUR-KHLIEHRIAT TL | 17/Oct/2026 | 08:00 | 17/Oct/2026 | 17:30 |  | SD may be availed subject to availability of 132kV Badarpur – Panchgram – Lunshnong-Khliehriat link, 132kV Khandong – Khleihriat link,132kV Khleihriat(PG)-Khleihriat(ME) D/C and 220kV Killing – Mawngap D/C
228 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 16/Oct/2026 | 08:00 | 16/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
229 | OCC_242 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Jungle clearance at Tower - (12 &13) | 16/Oct/2026 | 08:00 | 16/Oct/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
230 | OCC_242 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Jungle clearance at Tower - (12 &13) | 16/Oct/2026 | 08:00 | 16/Oct/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
231 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 16/Oct/2026 | 07:00 | 16/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
232 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 16/Oct/2026 | 07:00 | 16/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
233 | OCC_242 | NAGALAND | 132KV-SANIS-WOKHA-1 | D | Vegetation Clearance | 17/Oct/2026 | 09:00 | 17/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link, 132kV Kohima-Zhadima-Chiephobozou-Wokha link and 132kV Doyang-Sanis.
234 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 17/Oct/2026 | 08:00 | 17/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
235 | OCC_242 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Disc changing & jumper repairing at T/Loc-132 | 17/Oct/2026 | 08:00 | 17/Oct/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link. Intimation to Assam
236 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 17/Oct/2026 | 07:00 | 17/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
237 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 17/Oct/2026 | 07:00 | 17/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
238 | OCC_242 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | C | Data Shutdown for Rectification of Lossy Span | 18/Oct/2026 | 10:30 | 19/Oct/2026 | 18:30 | Data Shutdown only required | Subject to diverison of services which are currently over Badarpur-Kolasib via Kumarghat - Karimganj - Badarpur
239 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 18/Oct/2026 | 08:00 | 18/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
240 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 18/Oct/2026 | 07:00 | 18/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
241 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 18/Oct/2026 | 07:00 | 18/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
242 | OCC_242 | NAGALAND | 132KV-DOYANG-SANIS-1 | D | Vegetation Clearance | 19/Oct/2026 | 09:00 | 19/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Kohima-Zhadima-Chiephobozou-Wokha-Sanis link. Intimation to NEEPCO
243 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 19/Oct/2026 | 08:00 | 19/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
244 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 19/Oct/2026 | 07:00 | 19/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
245 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 19/Oct/2026 | 07:00 | 19/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
246 | OCC_242 | NAGALAND | 132KV-DOYANG-SANIS-1 | D | Vegetation Clearance | 20/Oct/2026 | 09:00 | 20/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Mokokchung-Tuengsan-Kiphire-Meluri-Kohima link and 132kV Kohima-Zhadima-Chiephobozou-Wokha-Sanis link. Intimation to NEEPCO
247 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 20/Oct/2026 | 08:00 | 20/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
248 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 20/Oct/2026 | 07:00 | 20/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
249 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 20/Oct/2026 | 07:00 | 20/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
250 | OCC_242 | NEEPCO | AGBPP - STG 1 | C | Condenser cleaning and RLA of boilers | 23/Oct/2026 | 00:00 | 2026-11-02 | 23:59 |  | SD may be availed subject to consent of all beneficairies.
251 | OCC_242 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | C | Data Shutdown for Rectification of Lossy Span | 21/Oct/2026 | 10:30 | 22/Oct/2026 | 18:30 | Data Shutdown only required | Subject to availablity of Link Mariani - Mokokchung (PG) - Mokokchung (State) - Doyang -Dimapur
252 | OCC_242 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 110 to 108 | 21/Oct/2026 | 10:00 | 21/Oct/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
253 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 21/Oct/2026 | 08:00 | 21/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
254 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 21/Oct/2026 | 07:00 | 21/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
255 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 21/Oct/2026 | 07:00 | 21/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
256 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 22/Oct/2026 | 09:00 | 22/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
257 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 22/Oct/2026 | 08:00 | 22/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
258 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 22/Oct/2026 | 07:00 | 22/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
259 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 22/Oct/2026 | 07:00 | 22/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
260 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 23/Oct/2026 | 09:00 | 23/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
261 | OCC_242 | NEEPCO | HRSG - 4 OF AGTCCPP (STG UNIT 6) - UNIT 6 | C | Hydro Test | 23/Oct/2026 | 0:00 | 31/Oct/2026 | 23:59 |  | SD may be availed. Consent from Beneficiaries is required
262 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 23/Oct/2026 | 08:00 | 23/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
263 | OCC_242 | POWERGRID | 132KV-AIZWAL-LONGMOL-1 | D | 1. GIS Warranty Testing (CB timing, CB DCRM, DC CRM), SF6 Gas Quality Analysing. 2. Relay Testing (Main and backup). 2. Luangmual Bay LA stressed conductor dropper replacement work. 3. LA IR. 4. SF6 to Air Bushing IR. | 23/Oct/2026 | 7:00 | 23/Oct/2026 | 15:00 |  | SD may be availed subject to the availability of 132kV Melriat-Aizawl line, 132kV Kumarghat-Aizawl line, 132kV Badarpur-Kolasib-Aizawl link. The connectivity during shutdown of 132kV Aizawl PG-Luangmual TL are as follows: 1) Melriat PG-Sihhmui-Luangmual-Zuangtui Old 2) Luangmual-Melriat Mz-Khawiva(Lunglei)-Kawmzawl 3) Melriat PG-Zuangtui New-Bukpui(Serchhip)-E.Lugdar 4) Melriat PG-Saitual-Vankal-Khawzawl-Champhai Note: Th SD may be availed subjected to approval of FTC of Sihhmui-Luangmual-Zuangtui Old. Consent from Mizoram is required
264 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 23/Oct/2026 | 07:00 | 23/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
265 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 23/Oct/2026 | 07:00 | 23/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
266 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 24/Oct/2026 | 09:00 | 24/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
267 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 24/Oct/2026 | 08:00 | 24/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
268 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 24/Oct/2026 | 07:00 | 24/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
269 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 24/Oct/2026 | 07:00 | 24/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
270 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 25/Oct/2026 | 09:00 | 25/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
271 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 25/Oct/2026 | 08:00 | 25/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
272 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 25/Oct/2026 | 07:00 | 25/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
273 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 25/Oct/2026 | 07:00 | 25/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
274 | OCC_242 | POWERGRID | FILTER BANK 1 SUB BANK 1 at BNC | D | AMP | 26/Oct/2026 | 09:00 | 26/Oct/2026 | 17:00 |  | SD may be availed, NLDC consent is req.
275 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 26/Oct/2026 | 09:00 | 26/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
276 | OCC_242 | POWERGRID | 400KV-BISWANATH CHARIALI-SUBANSIRI-4 L/R@ BISWANATH CHARIALI - 400KV | D | AMP OF LINE REACTOR | 26/Oct/2026 | 09:00 | 26/Oct/2026 | 17:00 |  | SD may be availed.
277 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 26/Oct/2026 | 08:00 | 26/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
278 | OCC_242 | OTPCL | 400KV/132KV PALATANA-ICT-1 | D | Hot spot rectification in 132 KV ICT-1 isolator 207 89B | 26/Oct/2026 | 08:00 | 26/Oct/2026 | 17:00 | ICT-1 Shutdown along with 132 KV BUS-2 Shutdown | SD may be availed subject to availability of ICT-2. SPS realted to Outage/tripping of both 400/132 kV, 2x125 MVA ICTs at Palatana to be kept ON during the shutdown period if combined demand of Tripura including Bangladesh is more than 460 MW. Dia to be closed at Palatana after availing shutdown.
279 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 26/Oct/2026 | 08:00 | 26/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line.
280 | OCC_242 | OTPCL | PALATANA - 132KV - BUS 2 | C | Hot spot Rectification in 132 KV ICT-1 Bus isolator 207-89B | 26/Oct/2026 | 08:00 | 27/Oct/2026 | 17:00 | Hotspot rectification | SD may be availed all elements to remain in service via other Bus. All elememnts to be shifted in online mode only
281 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 26/Oct/2026 | 08:00 | 26/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
282 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 26/Oct/2026 | 07:00 | 26/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
283 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 26/Oct/2026 | 07:00 | 26/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
284 | OCC_242 | OTPCL | 132KV/6.6KV PALATANA-ICT-1 | D | Hot spot rectification in 132 KV ICT-1 isolator 207 89B | 26/Oct/2026 | 00:00 | 26/Oct/2026 | 17:00 | ICT-1 Shutdown along with 132 KV BUS-2 Shutdown | SD may be availed subject to availability of 132/6.6kV SST-2 at Palatana
285 | OCC_242 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEANING LOC 58-102 | 27/Oct/2026 | 10:00 | 27/Oct/2026 | 17:00 | AGM TSK | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
286 | OCC_242 | POWERGRID | FILTER BANK 1 SUB BANK 2 at BNC | D | AMP | 27/Oct/2026 | 09:00 | 27/Oct/2026 | 17:00 |  | SD may be availed, NLDC consent req.
287 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 27/Oct/2026 | 09:00 | 27/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
288 | OCC_242 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 27/Oct/2026 | 09:00 | 27/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
289 | OCC_242 | AEGCL | 220KV-AZARA-BOKO-1 | D | CORRIDOR CLEANING LOC 284-209 | 27/Oct/2026 | 08:30 | 27/Oct/2026 | 16:30 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Mirza line to be kept in service
290 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 27/Oct/2026 | 08:00 | 27/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
291 | OCC_242 | OTPCL | 400KV/132KV PALATANA-ICT-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 27/Oct/2026 | 08:00 | 27/Oct/2026 | 17:00 | ICT-1 Shutdown along with 132 KV BUS-2 Shutdown | SD may be availed subject to availability of ICT-2. SPS realted to Outage/tripping of both 400/132 kV, 2x125 MVA ICTs at Palatana to be kept ON during the shutdown period if combined demand of Tripura including Bangladesh is more than 460 MW. Dia to be closed at Palatana after availing shutdown.
292 | OCC_242 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | C | CB Mechanism Overhauling at S.M. Nagar end | 27/Oct/2026 | 08:00 | 31/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time. | SD deferred and SD may be clubbed with 400kV palatana-SM nagar line SD (Line shitfing from ERS tower) | High loading observed in 132kV Palatana Udaipur, either 132kV Palatana-Udaipur to be opened during peak hours or This SD should be clubbed with Palatana Module SD which will also increase Monarchak genertion and might avoid over loading on 132kV Palatana-Udaipur.
293 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 27/Oct/2026 | 08:00 | 27/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line. Consent from Nagaland
294 | OCC_242 | Arunachal Pradesh | 132KV-KAMENG-KHUPI-1 | C | Re-conductoring | 27/Oct/2026 | 08:00 | 31/Oct/2026 | 16:00 |  | SD may be availed subject to availability of 132kv Balipara-Tenga-Khupi link. Intimation to NEEPCO and NERTS, FTC procedure to followed . Inimation to NEEPCO
295 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 27/Oct/2026 | 08:00 | 27/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
296 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 27/Oct/2026 | 07:00 | 27/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
297 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 27/Oct/2026 | 07:00 | 27/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
298 | OCC_242 | OTPCL | 132KV/6.6KV PALATANA-ICT-1 | D | Hot spot rectification in 132 KV ICT-1 isolator 207 89B | 27/Oct/2026 | 00:00 | 27/Oct/2026 | 17:00 | ICT-1 Shutdown along with 132 KV BUS-2 Shutdown | SD may be availed subject to availability of 132/6.6kV SST-2 at Palatana
299 | OCC_242 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 107 to 105 | 28/Oct/2026 | 10:00 | 28/Oct/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
300 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | D | Construction of 765 kV D/c Dausa-Ghiror TL(Part-III):For crossing of Earth electrod line -i | 28/Oct/2026 | 8:00 | 28/Oct/2026 | 12:00 |  | SD may be availed subject to availability of 400kV BNC-Balipara-Bongaigaon link, 400kV Bongaingaon-APD D/C, 400kV Bongaingaon-New siliguri D/C, 400kV Bongaingaon-Azara line, SD to be strictly adhered to approved timings.
301 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | D | Construction of 765 kV D/c Dausa-Ghiror TL(Part-III):For crossing of Earth electrod line -i | 28/Oct/2026 | 8:00 | 28/Oct/2026 | 12:00
302 | OCC_242 | POWERGRID | FILTER BANK 1 SUB BANK 4 at BNC | D | AMP | 28/Oct/2026 | 09:00 | 28/Oct/2026 | 17:00 |  | SD may be availed, NLDC consent req.
303 | OCC_242 | AEGCL | 220KV-AGIA-BTPS-2 | D | PREVENTIVE MAINTENANCE &CORRIDOR CLEANING | 25/Oct/2026 | 7:00 | 25/Oct/2026 | 14:00 | AGM GOAPT&T | S/D may be availed subject to availability of 220kV Agia-BTPS 1 line, 400kV Bongaigaon - Azara, 400kV Silchar - Azara,400/220kV ICTs at Azara S/s should be kept in service. Combined loading of 400kV Bongaigaon-Mirza line and Agia-BTPS-1 to be maintained within 350 MW. Generation of Karbi Langpi needs to be scheduled. The SD will be deferred when the NER demand is high
304 | OCC_242 | NAGALAND | 132KV-TUENSANG GIS-KIPHIRE-1 | D | Vegetation Clearance | 28/Oct/2026 | 09:00 | 28/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Dimapur-Kohima line, either of 132kV Imphal (Yurembam)-Ghampajol-Karong-Kohima link or 132kV Doyang-Sanis-wokha-Chiephobozou-Zhadima-Kohima link, 132kV Mokokchung-Tuengsan line and 132kV Kiphire-Meluri-Kohima link
305 | OCC_242 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 28/Oct/2026 | 09:00 | 28/Oct/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
306 | OCC_242 | POWERGRID | BUS COUPLER BAY (1) OF MISA - 220KV - BUS 1 AND MISA - 220KV - BUS 2 @MISA - 220KV | C | SAS UPGRADATION WORK UNDER ADD-CAP | 28/Oct/2026 | 09:00 | 31/Oct/2026 | 17:00 |  | Sd may be availed subject to no outage of elements.
307 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 28/Oct/2026 | 08:00 | 28/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
308 | OCC_242 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 199-249 & 69-100 | 28/Oct/2026 | 08:00 | 28/Oct/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
309 | OCC_242 | POWERGRID | 220KV-MARIANI (PG)-MOKOKCHUNG-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.87,88,98,99,100,101,102,104,105 | 28/Oct/2026 | 08:00 | 28/Oct/2026 | 16:30 |  | SD may be availed subject to the availability of 132KV-MOKOKCHUNG (PG)-MOKOKCHUNG-1 and 132kV Doyang-Mokokchung line.
310 | OCC_242 | POWERGRID | A/R of 220KV-MARIANI (PG)-MOKOKCHUNG-1 | D | A/R IN NON AUTO REQUIRED FOR WORK IN OTHER CIRCUIT | 28/Oct/2026 | 08:00 | 28/Oct/2026 | 16:30 | ONLY AR IN NON-AUTO REQUIRED, SHTDOWN NOT REQUIRED | A/R may be kept in Non-auto mode
311 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 28/Oct/2026 | 07:00 | 28/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
312 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 28/Oct/2026 | 07:00 | 28/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
313 | OCC_242 | POWERGRID | NAMSAI - 132KV B/R 1 | D | REPLACEMENT OF FAULTY MOG IN R-PHASE BANK OF THE REACTOR ALONG WITH AMP | 28/Oct/2026 | 07:00 | 28/Oct/2026 | 23:00 |  | SD may be availed
314 | OCC_242 | POWERGRID | FILTER BANK 2 SUB BANK 1 at BNC | D | AMP | 29/Oct/2026 | 09:00 | 29/Oct/2026 | 17:00 |  | SD nay be availed, NLDC consent req.
315 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 29/Oct/2026 | 08:00 | 29/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
316 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 29/Oct/2026 | 07:00 | 29/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
317 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 29/Oct/2026 | 07:00 | 29/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
318 | OCC_242 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEANING LOC 1-50 | 30/Oct/2026 | 10:00 | 30/Oct/2026 | 17:00 | AGM TSK | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
319 | OCC_242 | POWERGRID | FILTER BANK 2 SUB BANK 2 at BNC | D | AMP | 30/Oct/2026 | 09:00 | 30/Oct/2026 | 17:00 |  | SD nay be availed, NLDC consent req.
320 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | D | Construction of 765 kV D/c Dausa-Ghiror TL(Part-III):For crossing of Earth electrod line -i | 30/Oct/2026 | 8:00 | 30/Oct/2026 | 12:00 |  | SD may be availed subject to availability of 400kV BNC-Balipara-Bongaigaon link, 400kV Bongaingaon-APD D/C, 400kV Bongaingaon-New siliguri D/C, 400kV Bongaingaon-Azara line, SD to be strictly adhered to approved timings.
321 | OCC_242 | NRTS/NRPC | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | D | Construction of 765 kV D/c Dausa-Ghiror TL(Part-III):For crossing of Earth electrod line -i | 30/Oct/2026 | 8:00 | 30/Oct/2026 | 12:00
322 | OCC_242 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | PREVENTIVE MAINTENANCE &CORRIDOR CLEANING | 30/Oct/2026 | 09:00 | 30/Oct/2026 | 16:00 | AGM GOAPT&T & AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
323 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 30/Oct/2026 | 08:00 | 30/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
324 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 30/Oct/2026 | 07:00 | 30/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
325 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 30/Oct/2026 | 07:00 | 30/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode
326 | OCC_242 | POWERGRID | FILTER BANK 2 SUB BANK 3 at BNC | D | AMP | 31/Oct/2026 | 09:00 | 31/Oct/2026 | 17:00 |  | SD nay be availed, NLDC consent req.
327 | OCC_242 | NAGALAND | 132KV-MELURI-KIPHIRE-1 | D | Vegetation Clearance | 31/Oct/2026 | 09:00 | 31/Oct/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Mokokchung-Tuengsan-Kiphire link and 132kV Meluri-Kohima line
328 | OCC_242 | POWERGRID | A/R of 132KV-TEZU-NAMSAI-1 | D | Auto Reclosure in 132 KV Tezu- Namsai to be switch off to facilitate safe Stringing works of 132 kV Tezu - Namsai 2nd Circuit Under NERES -XXIII | 31/Oct/2026 | 08:00 | 31/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
329 | OCC_242 | POWERGRID | A/R of 132KV-PASIGHAT-ROING-1 | D | AR to be kept in non-auto mode to facilitate 2nd ckt stringing of 132kV Pasighat-Roing TL under project NERES-XXIII. | 31/Oct/2026 | 07:00 | 31/Oct/2026 | 17:00 | Shutdown not Required AR to be kept in Non-Auto Mode only | A/R may be kept in Non-auto mode
330 | OCC_242 | POWERGRID | A/R of 132KV-ROING-TEZU-1 | D | AR kept to be in non-auto mode to facilitate 2nd ckt stringing of 132kV Roing Tezu TL under project NERES-XXIII. | 31/Oct/2026 | 07:00 | 31/Oct/2026 | 17:00 | Shutdown not required. AR to be kept in Non-Auto | A/R may be kept in Non-auto mode