## Sheet1
Sl No | OCC Number | Name of Requesting Agency | Element Name | Daily/ Continous | Reason | Shutdown Start Date | Shutdown Start Time | Shutdown End Date | Shutdown End Time | Requester Remarks | Study Comments | Remarks
1 | OCC_243 | POWERGRID | 220KV-MISA-KOPILI-1 | C | Data Shutdown for Rectification of Lossy Span | 01/Nov/2026 | 10:30 | 01/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subject to availability of Misa - Kopili-2 & Misa - balipara. Services diversion via Misa-Kopili-2 or Misa - balipara
2 | OCC_243 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 01/Nov/2026 | 09:00 | 01/Nov/2026 | 16:00 | Shutdown required along with 132kV Monarchak - Rokhia Line | SD may be availed subject to the availability of 132kV Monarchak - Rabindranagar - Belonia-Bokafa-udaipur, 132kV Rabindranagar - Rokhia line, 132kV Palatana-Udaipur line and 132kV Rokhia - Agartala D/C line, Monarchak generation to be kept within 75 MW during SD period.
3 | OCC_243 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 01/Nov/2026 | 09:00 | 01/Nov/2026 | 16:00 | Shutdown required along with 132kV Monarchak - Udaipur Line
4 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 01/Nov/2026 | 7:00 | 01/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link
5 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 01/Nov/2026 | 08:00 | 01/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
6 | OCC_243 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | C | Facilitating de-stringing & stringing works related to diversion of Section of 132 kV S/C Dimapur – Imphal TL under Imphal jurisdiction in view of shifting of endangered tower Location No. 278. | 01/Nov/2026 | 08:00 | 11/Nov/2026 | 16:00 |  | SD may availed subject to availability of both the 400/132 kV ICTs at Imphal. FTC pocedure to be followed before charging of the line
7 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 01/Nov/2026 | 07:00 | 01/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
8 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 01/Nov/2026 | 07:00 | 01/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
9 | OCC_243 | NHPC | 132KV/11KV LOKTAK-ICT-1 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59 |  | SD may be availed.
10 | OCC_243 | NEEPCO | AGTCCPP - GTG 1 | C | Generator Stator Rewinding | 01/Nov/2026 | 00:00 | 16/Dec/2026 | 22:00 |  | SD may be availed, Consent required from all beneficiaries
11 | OCC_243 | POWERGRID | BUS COUPLER BAY (1) OF MISA - 220KV - BUS 1 AND MISA - 220KV - BUS 2 @MISA - 220KV | C | SAS UPGRADATION WORK UNDER ADD-CAP | 01/Nov/2026 | 00:00 | 03/Nov/2026 | 17:00 |  | SD may be availed, elements should be segregated in following way Bus 1: Two 220kV Misa-Kopili lines, One Misa-Samaguri line, One Misa-Dimapur line, One 220kV Misa-Killing line, and One 500 MVA 400/220kV Misa ICT. Bus 2: One 220kV Misa-Kopili line, One Misa-Samaguri line, One Misa-Dimapur line, One 220kV Misa-Killing line, One 500 MVA 400/220kV Misa ICT, and One 315 MVA 400/220kV ICT.
12 | OCC_243 | NHPC | LOKTAK - UNIT 1 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 31/Jul/2027 | 23:59 |  | SD may be availed, present status of power supply arrangement to Rengpang area required from Powergrid.
13 | OCC_243 | NHPC | LOKTAK - 132KV - BUS 1 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
14 | OCC_243 | NHPC | LOKTAK - 132KV - BUS 2 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
15 | OCC_243 | NHPC | BUS COUPLER BAY OF LOKTAK - 132KV - BUS 1 AND LOKTAK - 132KV - BUS 2 @LOKTAK - 132KV | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
16 | OCC_243 | NHPC | LOKTAK - UNIT 2 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
17 | OCC_243 | NHPC | LOKTAK - UNIT 3 | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
18 | OCC_243 | nhpc | 132 KV IMPHAL 1 BAY AT LOKTAK | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
19 | OCC_243 | nhpc | 132 KV IMPHAL 2 BAY AT LOKTAK | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
20 | OCC_243 | nhpc | 132 KV JIRIBAM(MA) BAY AT LOKTAK | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
21 | OCC_243 | nhpc | 132 KV JIRIBAM(PG)(RENGPANG) BAY AT LOKTAK | C | For R&M of Loktak PS | 03/Nov/2026 | 00:00 | 30/Apr/2027 | 23:59
22 | OCC_243 | POWERGRID | 220KV MAIN BAY OF 220KV/132KV SALAKATI-ICT-3 @SALAKATI - 220KV | D | AMP OF BAY EQUIPMENTS. | 02/Nov/2026 | 09:00 | 02/Nov/2026 | 17:00 |  | SD may be availed subject to no outage of elements.
23 | OCC_243 | POWERGRID | BUS COUPLER BAY () OF BALIPARA - 220KV - BUS 1 AND BALIPARA - 220KV - BUS 2 @BALIPARA - 220KV | D | Bay Equipment AMP work | 02/Nov/2026 | 8:00 | 02/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements. Elements to be segregatted properly in both bus. One 220kV Balipara-Sonabil line, 400/220kV ICT-1 & 220/132kV ICT-1 in one bus and remaining elements in other bus.
24 | OCC_243 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 1 | D | bay AMP: CT tan delta, CB testing | 02/Nov/2026 | 7:00 | 02/Nov/2026 | 16:00 | 400kV Bus Sectionalizer 1 Shutdown required | SD may be availed subject to availability of Sectionalizer 2 and all the dias should be in service, Considering N-1 contigency of other bus sectionalizer HVDC flow of single pole to be kept 250 MW, subansiri scheduled generation to be 500 MW during SD period.
25 | OCC_243 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | Routine Maintenance Work | 02/Nov/2026 | 09:00 | 02/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Assam
26 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 02/Nov/2026 | 7:00 | 02/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link. Intimation to NEEPCO
27 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 02/Nov/2026 | 08:00 | 02/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
28 | OCC_243 | NAGALAND | 132KV-DOYANG-MOKOKCHUNG-1 | D | vegetation Clearance | 02/Nov/2026 | 08:00 | 02/Nov/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV Mokokchung(NL)-Mokokchung(PG) D/C. Intimation to NEEPCO
29 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation Clearance | 02/Nov/2026 | 08:00 | 02/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
30 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 02/Nov/2026 | 07:00 | 02/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode Deferred due to Along-Pasighat SD. | Deferred due to Along-Pasighat SD.
31 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 02/Nov/2026 | 07:00 | 02/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
32 | OCC_243 | NEEPCO | AGBPP - GTG 5 | C | HOT GAS PATH INSPECTION | 02/Nov/2026 | 00:00 | 27/Nov/2026 | 00:00 | SHUTDOWN DURATION CORRECTED | Sd may be availed. Consent from beneificiary is required.
33 | OCC_243 | NEEPCO | AGBPP - GTG 5 | C | Hot Gas Inspection | 02/Nov/2026 | 00:00 | 26/Nov/2026 | 00:00 |  | Sd may be availed. Consent from beneificiary is required. | SD is wrong punched as informed by NEEPCO
34 | OCC_243 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 23/Nov/2026 | 09:00 | 23/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line, 132kV Aizwal-Tipaimukh-Jiribam link & 132kV Badarpur-Jiribam line.
35 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 101 TO 149 | 02/Nov/2026 | 08:00 | 02/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
36 | OCC_243 | POWERGRID | 132KV MAIN BAY OF 220KV/132KV SALAKATI-ICT-3 @SALAKATI - 132KV | D | AMP OF BAY EQUIPMENTS. | 03/Nov/2026 | 09:00 | 03/Nov/2026 | 17:00 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
37 | OCC_243 | TSECL | 132KV-MONARCHAK-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 03/Nov/2026 | 09:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link,132kV Monarchak - Rabindranagar - Belonia-Bokafa, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line
38 | OCC_243 | POWERGRID | FILTER BANK 2 SUB BANK 1 at BNC | D | bay AMP: CT tan delta, CB testing, RLC measurement of filter | 03/Nov/2026 | 09:00 | 03/Nov/2026 | 17:00 |  | SD nay be availed, NLDC consent req.
39 | OCC_243 | NAGALAND | 132KV-MELURI-KIPHIRE-1 | D | Vegetayion Clearance | 03/Nov/2026 | 09:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Mokokchung-Tuengsan-Kiphire link and 132kV Meluri-Kohima line
40 | OCC_243 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Routine Maintenance Work | 03/Nov/2026 | 09:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS), 132kV Surajmaninagar(ISTS)-Budhjungnagar and 132kV PKbari-Manu-Ambassa-Gamaitila-Barmura-Jiranaia-Budhjungnagar link. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
41 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 03/Nov/2026 | 7:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link
42 | OCC_243 | POWERGRID | MAIN BAY () OF 400KV/220KV MARIANI (PG)-ICT-2 @MARIANI (PG) - 400KV(409) | D | AMP of bay equipment | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
43 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
44 | OCC_243 | POWERGRID | 132KV-NEHU-UMIAM-1 | C | Data Shutdown for Rectification of Lossy Span | 03/Nov/2026 | 08:00 | 10/Nov/2026 | 16:00 | Required for 132 kV Nehu- Khliehriat | Subjec to the availablity of 132 kV Kheliriat - NERLDC Shillong and diversion of the services over 132 kV Kheliriat - NERLDC Shillong
45 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation Clearance | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
46 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 03/Nov/2026 | 07:00 | 03/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode Deferred due to Along-Pasighat SD. | Deferred due to Along-Pasighat SD.
47 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 03/Nov/2026 | 07:00 | 03/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
48 | OCC_243 | AEGCL | 132KV-SRIKONA-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 24/Nov/2026 | 09:00 | 24/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to availability of 132 kV Jiribam-Pailapool line, 132kV Aizwal-Tipaimukh-Jiribam link & 132kV Badarpur-Jiribam line.
49 | OCC_243 | AEGCL | 220KV-CHAYGAON GSS-AZARA-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 234 TO 244 | 03/Nov/2026 | 08:30 | 03/Nov/2026 | 16:30 | AGM SSJI | S/D may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Agia-Chaygaon line.
50 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 101 TO 149 | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
51 | OCC_243 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | ROUTINE TESTING OF BAY EQUIPMENTS & CORRIDOR CLEARANCE LOC 1 TO 30 | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 16:00 | AGM TINSUKIA | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
52 | OCC_243 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 334/5 TO 442 | 03/Nov/2026 | 08:00 | 03/Nov/2026 | 16:00 | AGM MARIANI | SD may be availed subject to availability of 220 kV Amguri-NTPS line, 220kV AGBPP-Mariani(As) line, 220kV AGBPP-Mariani(PG) line & 220kV Mariani(PG)-Mariani(As) line, Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 250 MW (during solar period) and 270 MW (during non-solar period)
53 | OCC_243 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 87 to 85. | 04/Nov/2026 | 10:00 | 04/Nov/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
54 | OCC_243 | POWERGRID | 220 KV BUS COUPLER BAY AT DIMAPUR (PG) | D | GIS Bay Warranty Tests | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
55 | OCC_243 | TSECL | 132KV-PALATANA-UDAIPUR (BANDUAR)-1 | D | Routine Maintenance Work | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Monarchak-rokhia link, 132kV Monarchak-Udaipur, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala D/C line. Intimation to OTPC
56 | OCC_243 | POWERGRID | DIMAPUR (PG) - 220KV - BUS 1 | D | GIS Bay Warranty Tests | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 17:00 |  | SD may be availed subject to availability of all elements via Dimapur(PG) bus 2.
57 | OCC_243 | POWERGRID | FILTER BANK 3 SUB BANK 3 at BNC | D | bay AMP: CT tan delta, CB testing, RLC measurement of filter | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 17:00 |  | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required
58 | OCC_243 | POWERGRID | 400KV/220KV MISA-ICT-2 | D | For Replacement of aircell and AMP of 220 kV side bay | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 22:00 |  | SD may be availed subject to the availability of 400/220kV ICT 1 and ICT 3 at Misa.
59 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 04/Nov/2026 | 09:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
60 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 04/Nov/2026 | 7:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link
61 | OCC_243 | POWERGRID | MAIN BAY (410) OF 400KV-NEW KOHIMA-MARIANI (PG)-1 @MARIANI (PG) - 400KV | D | AMP of bay equipment | 04/Nov/2026 | 08:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
62 | OCC_243 | POWERGRID | MAIN BAY (205) OF 400KV/220KV BALIPARA-ICT-2 @BALIPARA - 220KV | D | Bay Equipment and ICT AMP | 04/Nov/2026 | 7:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subjected to the availability of 400/220kV 315MVA ICT-1 at Balipara, 220kV Samaguri-Misa DC lines and 220kV Mirza-Sarusajai DC line. Considering N-1 contigency of 400/220kV ICT-2 at Balipara samaguri gate flow to be maintained within 420 MW during SD period. Lower Kopili generation during the SD will aid to reliability of system, Consent required from Assam.
63 | OCC_243 | POWERGRID | MAIN BAY (401) OF 400KV/220KV BALIPARA-ICT-2 AND @BALIPARA - 400KV | D | Bay Equipment and ICT AMP | 04/Nov/2026 | 7:00 | 04/Nov/2026 | 16:00
64 | OCC_243 | POWERGRID | TIE BAY () OF 220KV/132KV BALIPARA-ICT-2 AND BALIPARA - 400KV B/R 2 @BALIPARA - 400KV | D | Bay Equipment and ICT AMP | 04/Nov/2026 | 7:00 | 04/Nov/2026 | 16:00 | THIS is 400/220 kV ICT-2 AT BALIPARA INSTEAD OF 220 KV/ 132 KV BALIPARA ICT-2
65 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 04/Nov/2026 | 08:00 | 04/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
66 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation Clearance | 04/Nov/2026 | 08:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link, 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link and 132kV Tinsukia-Rupai-Chapakhowa-Roing link
67 | OCC_243 | POWERGRID | 400KV/220KV BALIPARA-ICT-2 | D | Bay Equipment and ICT AMP | 04/Nov/2026 | 7:00 | 04/Nov/2026 | 16:00 |  | SD may be availed subjected to the availability of 400/220kV 315MVA ICT-1 at Balipara, 220kV Samaguri-Misa DC lines and 220kV Mirza-Sarusajai DC line. Considering N-1 contigency of 400/220kV ICT-2 at Balipara samaguri gate flow to be maintained within 420 MW during SD period. Lower Kopili generation during the SD will aid to reliability of system, Consent required from Assam.
68 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 04/Nov/2026 | 07:00 | 04/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode SD deferred due to Along-Pasighat SD | SD deferred due to Along-Pasighat SD
69 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 04/Nov/2026 | 07:00 | 04/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
70 | OCC_243 | NEEPCO | AGBPP - STG 3 | C | CONDENSER CLEANING AND RLA OF BOILERS | 04/Nov/2026 | 00:00 | 15/Nov/2026 | 00:00 | SHUTDOWN DURATION CORRECTED | SD may be availed, consent required from all beneficiaries | SD deferred as NEEPCO won't be availing the SD
71 | OCC_243 | NEEPCO | AGBPP - STG 3 | C | CONDENSER CLEANING AND RLA OF BOILERS | 04/Nov/2026 | 00:00 | 14/Nov/2026 | 00:00 |  | SD may be availed, consent required from all beneficiaries | SD is wrong punched as informed by NEEPCO
72 | OCC_243 | AEGCL | 132KV-RUPAI-MARGHERITA_AS-1 | D | MAINTENANCE & REPAIRING WORK LOC 72-73 | 11/Nov/2026 | 09:00 | 11/Nov/2026 | 16:00 | LEDO | S/D may be availed subject to the availability of 132kV Tinsukia-Rupai and 132kV Tinsukia-Margherita, 132kV Roing-Chapakhowa-Rupai link, Kathalguri-Namsai-Tezu-Roing link.
73 | OCC_243 | POWERGRID | 132KV-RANGANADI-ZIRO-1 | C | Data Shutdown for Rectification of Lossy Span | 05/Nov/2026 | 10:30 | 07/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subjec to the availablity of 132 kV Ziro - Daporizo - Basar - Along - Pasighat - Roing - Tezu - Namsai - NERLDC
74 | OCC_243 | TSECL | 132KV-MONARCHAK-ROKHIA-1 | D | Routine Maintenance Work | 05/Nov/2026 | 09:00 | 05/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Monarchak - Udaipur-Palatana link, 132kV Monarchak - Rabindranagar - Belonia-Bokafa-Udaipur link, 132kV Rabindranagar - Rokhia line and 132kV Rokhia - Agartala link.
75 | OCC_243 | POWERGRID | 220KV-MISA-KOPILI-3 | C | SAS upgradation (1. Existing cable dismantle and new cable termination, Shifting of PLCC panel, DC/AC termination from DCDB(48 & 220 V)/ACDB, M1 and M2 protection test (Day1-Day 9) with main bay. From 10-11th day, BusA sd will be proposed for testing of LBB /Busbar and protection Transfer scheme | 05/Nov/2026 | 09:00 | 16/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV Misa-Kopili Ckt 1 and 2
76 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 05/Nov/2026 | 09:00 | 05/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
77 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 05/Nov/2026 | 7:00 | 05/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link
78 | OCC_243 | POWERGRID | TIE BAY (411) OF 400KV-NEW KOHIMA-MARIANI (PG)-1 AND MARIANI (PG) - 400KV B/R 2 @MARIANI (PG) - 400KV | D | AMP of bay equipment | 05/Nov/2026 | 08:00 | 05/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
79 | OCC_243 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 2 | D | bay AMP: CT tan delta, CB testing in sectionalizer | 05/Nov/2026 | 6:00 | 05/Nov/2026 | 16:00 | 400kV Bus 2A & Bus 2 Sectionalizer shutdown required | SD may be availed subject to the availability of all elements via Bus-1A. All the dias should be in service, Considering N-1 contigency of Bus 1A combined loading of AP capital area and Assam gohpur area to be restricted within 150 MW without Pare and Panyor m/c, with one machine of Pare and Panyor each load can be kept up to 220 MW.. Considering N-1 contigency of Bus1 sectionalizer HVDC flow of single pole to be kept 250 MW subansiri scheduled generation to be 500 MW during SD period.
80 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 05/Nov/2026 | 08:00 | 05/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
81 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-PASIGHAT-1 | D | Vegetation Clearance | 05/Nov/2026 | 08:00 | 05/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Panyor-Ziro-Daporizo-Basar-Along link and 132kV Kathalguri-Namsai-Tezu-Roing-Pasighat link
82 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 05/Nov/2026 | 07:30 | 05/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat-2 & 132kV Aizwal-Melriat.
83 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 05/Nov/2026 | 07:00 | 05/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | SD deferred due to sd of 132KV-ALONG-PASIGHAT-1 | Sd deferred
84 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 05/Nov/2026 | 07:00 | 05/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
85 | OCC_243 | AEGCL | 132KV-GOLAGHAT-MARIANI (AS)-1 | D | CORRIDOR CLEANING | 05/Nov/2026 | 09:00 | 05/Nov/2026 | 16:00 | RE GLG | S/D may be availed. 132 kV Dimapur - Bokajan - Sarupathar - Golaghat link to be kept in service.
86 | OCC_243 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 25/Nov/2026 | 09:00 | 25/Nov/2026 | 16:00 | RE PAILAPOOL | S/D may be availed subject to 132kV Srikona-Pailapool.
87 | OCC_243 | AEGCL | 132KV-JIRIBAM(PG)-PAILAPPOL-1 | D | PREVENTIVE MAINTENANCE | 05/Nov/2026 | 09:00 | 05/Nov/2026 | 16:00 | RE PAILAPOOL | S/D may be availed subject to 132kV Srikona-Pailapool. | SD deferred as punching done twice
88 | OCC_243 | AEGCL | 220KV-MARIANI (AS)-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 334/5 TO 442 | 05/Nov/2026 | 08:00 | 05/Nov/2026 | 16:00 | AGM MARIANI | SD may be availed subject to availability of 220 kV Amguri-NTPS line. Considering N-1 contingency of 220 kV AGBPP - Mariani (PG) line, Upper Assam Power Flow is to be maintained within 250 MW (during solar period) and 270 MW (during non-solar period)
89 | OCC_243 | POWERGRID | 132KV-RANGIA-DEOTHANG-1 | D | AMP OF BAY EQUIPMENTS. | 06/Nov/2026 | 10:00 | 06/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 220kV BTPS-Rangia D/C, Both the SPS at Rangia to be kept enabled, Assam, NLDC and Bhutan consent is required
90 | OCC_243 | TSECL | 132KV-DHARMANAGAR (MISSION TILLA)-P K BARI-1 | D | Routine Maintenance Work | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 16:00 |  | SD may be availed subject to availability of Hailakandi-Dullavcherra-Dharmanagar link. Intimation to Assam
91 | OCC_243 | POWERGRID | MAIN BAY (124) OF 220KV/132KV BALIPARA-ICT-2 @BALIPARA - 132KV | D | Bay Equipment and ICT PRV check | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 17:00 |  | Sd may be availed subject to the availability of 220/132kV ICT-1 at Balipara and 132kv Kameng-Khupi-Tenga-Balipara link. Intimation to AP is required
92 | OCC_243 | POWERGRID | MAIN BAY (220) OF 220KV/132KV BALIPARA-ICT-2 AND @BALIPARA - 220KV | D | Bay Equipment and ICT PRV check | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 17:00
93 | OCC_243 | POWERGRID | 220KV/132KV BALIPARA-ICT-2 | D | Bay Equipment and ICT PRV check | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 17:00
94 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
95 | OCC_243 | POWERGRID | 132KV-KHANDONG-UMRANSHU-1 | D | TLA installation in the whole line. | 06/Nov/2026 | 7:00 | 06/Nov/2026 | 16:00 |  | SD may be availed subject to the availabilty of 132kV Jiribam-Haflong(PG)-Umrangsho link
96 | OCC_243 | POWERGRID | BISWANATH CHARIALI - 400KV - BUS 2 | D | AMP | 06/Nov/2026 | 6:00 | 06/Nov/2026 | 16:00 | 400kV Bus 2A and Bus 2 Sectionalizer shutdown required | SD may be availed subject to the availability of all elements via Bus-1A. All the dias should be in service, Considering N-1 contigency of Bus 1A combined loading of AP capital area and Assam gohpur area to be restricted within 150 MW without Pare and Panyor m/c, with one machine of Pare and Panyor each load can be kept up to 220 MW.. Considering N-1 contigency of Bus1 sectionalizer HVDC flow of single pole to be kept 250 MW subansiri scheduled generation to be 500 MW during SD period.
97 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 06/Nov/2026 | 08:00 | 06/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
98 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 06/Nov/2026 | 07:30 | 06/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat-2 & 132kV Aizwal-Melriat.
99 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 06/Nov/2026 | 07:00 | 06/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
100 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 06/Nov/2026 | 07:00 | 06/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
101 | OCC_243 | NAGALAND | 132KV-DIMAPUR-DIMAPUR(PG)-2 | D | Annual Substation Manintainance | 06/Nov/2026 | 06:00 | 06/Nov/2026 | 09:00 |  | Sd may be availed. Dimapur(Nagarjan) will be dark during the SD period. Intimation to NERTS
102 | OCC_243 | NAGALAND | 132KV-DIMAPUR-DIMAPUR(PG)-1 | D | Annual Substation Manintainance | 06/Nov/2026 | 06:00 | 06/Nov/2026 | 09:00
103 | OCC_243 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya
104 | OCC_243 | AEGCL | 132KV-BOKAJAN-DIMAPUR(PG) | D | PREVENTIVE MAINTENANCE &CORRIDOR CLEANING | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 16:00 | RE BOKAJAN | S/D may be availed. 132 kV Mariani - Golaghat - Sarupathar - Bokajan link to be kept in service. Intimation to NERTS
105 | OCC_243 | AEGCL | 220KV/132KV TINSUKIA-ICT-1 | D | ROUTINE BAY TESTING | 06/Nov/2026 | 8:00 | 06/Nov/2026 | 16:00 | AGM TSK | SD may be availed subjec to availability of 220kV NTPS-Bordubi-Tinsukia link, 132kV Behiating-Dibrugarh-Tinsukia link, 132kV Tinsukia-Rupai-Chapakhowa-Roing link, 132kV Tinsukia-Ledo-Rupai link, Considering N-1 contigency of 220/132kV ICT-2 at Tinsukia combined loading of Tinsukia ICT-2 and 132kV NTPS-Bordubi line should be maintained below 100 MW, line loading of 132kV NTPS-Bordubi line to be maintained below 50 MW.
106 | OCC_243 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 228 TO 307 | 06/Nov/2026 | 08:00 | 06/Nov/2026 | 16:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Chaygaon - Mirza link to be kept in service
107 | OCC_243 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 314 TO 238 | 06/Nov/2026 | 08:00 | 06/Nov/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
108 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 07/Nov/2026 | 09:00 | 07/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
109 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 07/Nov/2026 | 7:00 | 07/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
110 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 07/Nov/2026 | 08:00 | 07/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
111 | OCC_243 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 07/Nov/2026 | 08:00 | 07/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
112 | OCC_243 | MEPTCL | NANGALBIBRA - 132KV - BUS 1 | D | Preventive maintenance of terminal equipments | 07/Nov/2026 | 08:00 | 07/Nov/2026 | 13:00 | Avail | SD may be availed subject to availability 132kV AGia – Mendipathar, 132kV Mawngap – Nongstoin, 132kV Agia – Hastingmari – Ampati – Rongkhon – Ganol link. Intimation to Assam
113 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 07/Nov/2026 | 07:30 | 07/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat-2 & 132kV Aizwal-Melriat.
114 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 07/Nov/2026 | 07:00 | 07/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | Sd deferred due to sd of 132KV-DAPORIJU-BASAR-1
115 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 07/Nov/2026 | 07:00 | 07/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
116 | OCC_243 | AEGCL | 132KV-RUPAI-CHAPAKHOWA-1 | D | CORRIDOR CLEANING LOC 1 TO 158 | 12/Nov/2026 | 09:30 | 12/Nov/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa and 132 kV Panyor - Ziro - Daporizo-Basar-Along-Pasighat-Roing link. Intimation to AP and NERTS
117 | OCC_243 | AEGCL | 132KV-LUMSNONG-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 07/Nov/2026 | 09:00 | 07/Nov/2026 | 16:00 | AGM PNG | S/D may be availed.132kV Lumshnong - Khlrihriat, 132 kV Badarpur-Khleihrait line, 132 kV Kopili-Khandong- Khliehriat link, 132 kV Jiribam - Halfong - Khandong - Khliehriat links, 220kV Mawngap - Killing D/C, 132kV Khliehriat(ME)-Khleihriat(PG) D/C line and 132kV Hailakandi - Panchgram - Badarpur link shall be kept in service. Consent from Meghalaya
118 | OCC_243 | AEGCL | 220KV-SONAPUR-SARUSAJAI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING 1 TO 42 | 07/Nov/2026 | 08:00 | 07/Nov/2026 | 16:00 | AGM SSJI | SD of 220kV Sarusajai-Sonapur line may be availed subject to availability of 220kV Samaguri-Sonapur, 220kV Samaguri-Jawaharnagar-Sarusajai link & 220kV Sarusajai-Azara D/C.
119 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 08/Nov/2026 | 09:00 | 08/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
120 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 08/Nov/2026 | 7:00 | 08/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
121 | OCC_243 | Arunachal Pradesh | 132KV-KAMENG-KHUPI-1 | C | Reconductoring of Kimi-Khuppi line | 08/Nov/2026 | 08:00 | 12/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kv Balipara-Tenga-Khupi link. Intimation to NEEPCO and NERTS, FTC procedure to followed . Inimation to NEEPCO
122 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 08/Nov/2026 | 08:00 | 08/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
123 | OCC_243 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 08/Nov/2026 | 08:00 | 08/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai-Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
124 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 08/Nov/2026 | 07:30 | 08/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV Silchar-Melriat-2 & 132kV Aizwal-Melriat.
125 | OCC_243 | POWERGRID | AR of132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 08/Nov/2026 | 07:00 | 08/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | Sd deferred due to sd of 132KV-DAPORIJU-BASAR-1
126 | OCC_243 | POWERGRID | AR of132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 08/Nov/2026 | 07:00 | 08/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
127 | OCC_243 | POWERGRID | MAIN BAY (404) OF 400KV/220KV BALIPARA-ICT-1 AND @BALIPARA - 400KV | D | Bay Equipment AMP | 09/Nov/2026 | 09:00 | 09/Nov/2026 | 17:00 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
128 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 09/Nov/2026 | 09:00 | 09/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
129 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 09/Nov/2026 | 7:00 | 09/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
130 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 09/Nov/2026 | 08:00 | 09/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
131 | OCC_243 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 09/Nov/2026 | 08:00 | 09/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai-Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
132 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 09/Nov/2026 | 07:30 | 09/Nov/2026 | 17:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
133 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 09/Nov/2026 | 07:00 | 09/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | Sd deferred due to sd of 132KV-DAPORIJU-BASAR-1
134 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 09/Nov/2026 | 07:00 | 09/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
135 | OCC_243 | NEEPCO | DOYANG - UNIT 3 | C | APM | 09/Nov/2026 | 00:00 | 03/Dec/2026 | 23:59 | APM | SD may be availed. Consent from beneficiaries required
136 | OCC_243 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 74 TO 32 | 09/Nov/2026 | 08:00 | 09/Nov/2026 | 16:00 | AGM SSJI & AGM SMG | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
137 | OCC_243 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 334/5 | 09/Nov/2026 | 08:00 | 09/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
138 | OCC_243 | POWERGRID | BUS COUPLER BAY () OF SALAKATI - 220KV - BUS 1 AND SALAKATI - 220KV - BUS 2 @SALAKATI - 220KV | D | AMP OF BAY EQUIPMENTS | 10/Nov/2026 | 09:30 | 10/Nov/2026 | 17:00 |  | Shutdown may be availed. Proper segregation of elements to be ensured before availing the shutdown.
139 | OCC_243 | NEEPCO | 220KV-AGBPP-MARIANI (AS)-1 | C | Replacement and retrofitting of new 245 KV,800/1 Current Transformer | 10/Nov/2026 | 09:00 | 13/Nov/2026 | 23:59 | CSD | SD may be availed subject to availability of 220kV AGBPP-Mariani(PG)-Mariani(As) link, 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(As) link, 220kV Mariani-Samaguri line & 132kV Mariani-Golaghat-Sarupathar-Bokajan-Dimapur link, Upper assam gate flow to be maintained within 260 MW.FTC procedure to be followed before charging of the line. Consent from Assam
140 | OCC_243 | POWERGRID | 400KV-SILCHAR-MISA-2 L/R@ MISA - 400KV | D | Oil filling /MOG replacement | 10/Nov/2026 | 09:00 | 10/Nov/2026 | 17:00 |  | SD may be availed
141 | OCC_243 | MEPTCL | 132KV-AGIA-MENDIPATHER-1 | D | Jungle cutting between T/Loc 273-289 | 10/Nov/2026 | 09:00 | 10/Nov/2026 | 16:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Nangalbibra, 132kV Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link. Intimation to Assam
142 | OCC_243 | NAGALAND | 132KV-KOHIMA-MELURI-1 | D | vegetation Clearance | 10/Nov/2026 | 09:00 | 10/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132 kV Yurembam-Gamphajol-Karong-Kohima link, 132 kV Dimapur-Kohima link, 132 kV Doyang-Sanis-Wokha-Chiephobozou-Zhadima-Kohima link and 132kV Mokokchung-Tuengis-Kiphire-Meluri link
143 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 10/Nov/2026 | 7:00 | 10/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
144 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 10/Nov/2026 | 08:00 | 10/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
145 | OCC_243 | POWERGRID | 132KV-JIRIBAM-LOKTAK-1 | C | Data Shutdown for Tower Diversion works | 10/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 |  | To be taken with Loktak Shutdown
146 | OCC_243 | Arunachal Pradesh | 132KV-DAPORIJU-BASAR-1 | D | Vegetation Clearance | 10/Nov/2026 | 08:00 | 10/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro-Daparijo, 132kV Basar-Along--Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai-Tinsukia link and Roing-Tezu-Namsai-Kathalguri link.
147 | OCC_243 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement with ACSR moose terminal connectors of all equipments. | 16/Nov/2026 | 08:00 | 16/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period. Consent from Assam
148 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 10/Nov/2026 | 07:30 | 10/Nov/2026 | 17:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
149 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 10/Nov/2026 | 07:00 | 10/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
150 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 10/Nov/2026 | 07:00 | 10/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
151 | OCC_243 | AEGCL | 132KV-SARUPATHAR-GOLAGHAT-1 | D | CORRIDOR CLEANING | 15/Nov/2026 | 09:00 | 15/Nov/2026 | 16:00 | RE GLG | S/D may availed. 132 kV Mariani - Golaghat line and 132 kV Dimapur - Bokajan - Sarupathar link to be kept in service.
152 | OCC_243 | AEGCL | 132KV-HAILAKANDI-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 10/Nov/2026 | 09:00 | 10/Nov/2026 | 16:00 | AGM PNG | SD May be availed subject to availability of 132 kV Khleiriat - Lumshnong -Panchgram link& 132 kV Panchgram - Badarpur.
153 | OCC_243 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 334/5 | 14/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
154 | OCC_243 | AEGCL | 220KV-AGBPP-TINSUKIA-2 | D | ROUTINE TESTING & CORRIDOR CLEARANCE LOC 53 TO 82 | 15/Nov/2026 | 08:00 | 15/Nov/2026 | 16:00 | AGM TINSUKIA | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri I, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
155 | OCC_243 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 10/Nov/2026 | 08:00 | 10/Nov/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
156 | OCC_243 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-1 | D | Tightening of nuts and bolts between Tower Location 84 to 82. | 11/Nov/2026 | 10:00 | 11/Nov/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-2
157 | OCC_243 | POWERGRID | 400 KV BISWANATH CHARIALI 3 MAIN BAY (415) AT BALIPARA | D | Bay Equipment AMP | 11/Nov/2026 | 09:00 | 11/Nov/2026 | 17:00 |  | SD may be availed, BNC 3 shares dia with Bongaigaon 1
158 | OCC_243 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | vegetation Clearance | 11/Nov/2026 | 09:00 | 11/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
159 | OCC_243 | POWERGRID | FILTER BANK 3 SUB BANK 4 at BNC | D | bay AMP: CT tan delta, CB testing, RLC measurement of filter | 11/Nov/2026 | 09:00 | 11/Nov/2026 | 17:00 |  | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required
160 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 11/Nov/2026 | 7:00 | 11/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
161 | OCC_243 | POWERGRID | MARIANI (AS) - 220KV - BUS 1 | D | 220KV POWERGRID bay's(202) existing Bus -A isolators ACSR Zebra terminal connectors replacement with ACSR moose terminal connectors | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220kV AGBPP-Mariani line, 132kV Rupai-Chapakhowa-Roing link, 132kV Nazira-Teok line, 132kV LTPS-Nazira D/C line, 132kV LTPS-Mariani line & 132kV LTPS-NTPS line, Upper Assam load to be kept below 350 MW during SD period considering N-1 contigency of other Mariani 220kV Bus.
162 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 11/Nov/2026 | 08:00 | 11/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
163 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | C | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 11/Nov/2026 | 08:00 | 30/Nov/2026 | 16:00 | Previously mistakenly gived Daily in place of continious. Kindly consider the continious shutdown. | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
164 | OCC_243 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement with ACSR moose terminal connectors of all equipments. | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period. Consent from Assam
165 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 11/Nov/2026 | 07:30 | 11/Nov/2026 | 17:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
166 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 11/Nov/2026 | 07:00 | 11/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
167 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 11/Nov/2026 | 07:00 | 11/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
168 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | C | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 11/Nov/2026 | 06:00 | 30/Nov/2026 | 23:59 | Previously mistakenly gived Daily in place of continious. Kindly consider the continious shutdown. | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period.
169 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | C | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 11/Nov/2026 | 06:00 | 14/Nov/2026 | 22:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
170 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 11/Nov/2026 | 06:00 | 11/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
171 | OCC_243 | POWERGRID | BUS COUPLER BAY () OF DIMAPUR (PG) GIS - 132KV - BUS 1 AND DIMAPUR (PG) GIS - 132KV - BUS 2 @DIMAPUR (PG) GIS - 132KV | D | GIS Bay Warranty Tests | 12/Nov/2026 | 09:00 | 12/Nov/2026 | 16:00 |  | SD may be availed subject to availability of all elements via Dimapur(PG) bus 1.
172 | OCC_243 | POWERGRID | DIMAPUR (PG) GIS - 132KV - BUS 2 | D | GIS Bay Warranty Tests | 12/Nov/2026 | 09:00 | 12/Nov/2026 | 16:00
173 | OCC_243 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | vegetation Clearance | 12/Nov/2026 | 09:00 | 12/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
174 | OCC_243 | POWERGRID | FILTER BANK 3 SUB BANK 5 at BNC | D | bay AMP: CT tan delta, CB testing, RLC measurement of filter | 12/Nov/2026 | 09:00 | 12/Nov/2026 | 17:00 |  | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required
175 | OCC_243 | TSECL | 132KV-BODHJUNGNAGAR-SURAJMANI NAGAR-1 | D | Routine Maintenance Work | 02/Nov/2026 | 09:00 | 02/Nov/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link.
176 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 12/Nov/2026 | 7:00 | 12/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
177 | OCC_243 | POWERGRID | MARIANI (AS) - 220KV - BUS 2 | D | 220KV POWERGRID bay's(202) existing Bus -A isolators ACSR Zebra terminal connectors replacement with ACSR moose terminal connectors | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Dimapur-Bokajan-Sarupathar-Golaghat-Mariani link, 220kV AGBPP-Mariani line, 132kV Rupai-Chapakhowa-Roing link, 132kV Nazira-Teok line, 132kV LTPS-Nazira D/C line, 132kV LTPS-Mariani line & 132kV LTPS-NTPS line, Upper Assam load to be kept below 350 MW during SD period considering N-1 contigency of other Mariani 220kV Bus.
178 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 12/Nov/2026 | 08:00 | 12/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
179 | OCC_243 | MEPTCL | 132KV-UMTRU-SARUSAJAI-1 | D | Hardware fitting at Tower (85 to 89) will be checked | 12/Nov/2026 | 08:00 | 12/Nov/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
180 | OCC_243 | MEPTCL | 132KV-UMTRU-SARUSAJAI-2 | D | Hardware fitting at Tower (85 to 89) will be checked | 12/Nov/2026 | 08:00 | 12/Nov/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
181 | OCC_243 | POWERGRID | 220KV-MARIANI (PG)-MARIANI (AS)-1 | D | Existing Zebra Terminal Connectors replacement with ACSR moose terminal connectors of all equipments. | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 220kV AGBPP-Mariani(AS), 220kV AGBPP-Mariani(PG), 220kV Mariani(AS)-Samaguri, 132kV Mariani(AS)-Golaghat-Sarupathar-Bokajan-Dimapur(PG) link, 220kV AGBPP-Namsai D/C line and 220kV AGBPP-Tinsukia-NTPS-Amguri-Mariani(AS) link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation. SD may be deferred during high demand period. Consent from Assam
182 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No. 218, 220 ,222,327, 328, 336, 337, 339, 340. | 12/Nov/2026 | 07:30 | 12/Nov/2026 | 17:00 |  | Sd may be availed subject to the availability of 132KV-SILCHAR-MELRIAT-1 and 132kv Aizawl-Melriat
183 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 12/Nov/2026 | 07:00 | 12/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
184 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 12/Nov/2026 | 07:00 | 12/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
185 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 12/Nov/2026 | 06:00 | 12/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
186 | OCC_243 | NEEPCO | MONARCHAK(THERMAL) - GTG 1 | C | Boiler Hydro test , GTG air inlet filter replacement, other E/M maintenance works | 12/Nov/2026 | 00:00 | 19/Nov/2026 | 23:59 |  | Sd may be availed. Consent from Tripura is required | Pending for approval
187 | OCC_243 | NEEPCO | MONARCHAK(THERMAL) - UNIT 2 | C | Boiler Hydro test , GTG air inlet filter replacement, other E/M maintenance works | 12/Nov/2026 | 00:00 | 19/Nov/2026 | 23:59 |  | Sd may be availed. Consent from Tripura is required | Pending for approval
188 | OCC_243 | AEGCL | 132KV-SARUPATHAR-BOKAJAN-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 20/Nov/2026 | 09:00 | 20/Nov/2026 | 16:00 | RE BOKAJAN | S/D may be availed. 132 kV Dimapur -Bokajan line and 132 kV Mariani - Golaghat - Sarupathar link to be kept in service
189 | OCC_243 | AEGCL | 220KV-JAWAHARNAGAR-SARUSAJAI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 35 TO 25 | 12/Nov/2026 | 08:00 | 12/Nov/2026 | 16:00 | AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Samaguri line.
190 | OCC_243 | AEGCL | 220KV-MARIANI (AS)-SAMAGURI-2 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 1 TO 334/5 | 19/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed. At present, the Upper Assam power system is connected with 220 kV Samaguri-Mariani(AS) line, 220 kV Mariani(AS) - Mariani (PG) line, 220 kV AGBPP-Mariani(PG) line and 132 kV Mariani - Golaghat - Sarupathar - Bokajan - Dimapur, 220kV Kathalguri - Namsai D/C and 132 kV Roing - Chapakhowa link. Under N-1 condition of 220 kV AGBPP-New Mariani (PG) , Gate flow should be monitored and shall be maintained below 260 MW(during solar period) and 240 MW (durng non-solar period) for safe and reliable grid operation.
191 | OCC_243 | POWERGRID | 132KV-SALAKATI-GELEPHU-1 | C | Data Shutdown for Rectification of Lossy Span | 13/Nov/2026 | 10:30 | 16/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span
192 | OCC_243 | POWERGRID | 400 KV BONGAIGAON 1 MAIN BAY (WITH 63 MVAR LINE REACTOR) (413) AT BALIPARA | D | Bay Equipment AMP | 13/Nov/2026 | 09:00 | 13/Nov/2026 | 17:00 | Only Bay required, 63 MVAR Line Reactor Not required | SD may be availed subject to no outage of element
193 | OCC_243 | POWERGRID | FILTER BANK1 MAIN BAY AT BNC | D | bay AMP: CT tan delta, CB testing | 13/Nov/2026 | 09:00 | 13/Nov/2026 | 17:00 |  | SD may be availed Subjected to no Power order restriction on HVDC, NLDC consent is required
194 | OCC_243 | NAGALAND | 132KV-DIMAPUR(PG)-KOHIMA-2 | D | vegetation Clearance | 13/Nov/2026 | 09:00 | 13/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Doyang-Sanis-Wokha-Chiephbozou-Kohima and either of 132kv Mokokchung-Tuensang-Kiphire-Meluri-Kohima or 132kV Imphal- Gamphazol-Karong-Kohima. Intimation to Powergrid.
195 | OCC_243 | TSECL | 132KV-PK BARI (INDIGRID)-MANU-1 | D | Routine Maintenance Work | 13/Nov/2026 | 09:00 | 13/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Budhjungangar- Jiriania - Gamaitila - Amabasa - Manu link. Intimation to INDIGRID
196 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 13/Nov/2026 | 7:00 | 13/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
197 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 13/Nov/2026 | 08:00 | 13/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
198 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-BASAR-1 | D | Vegetation Clearance | 13/Nov/2026 | 08:00 | 13/Nov/2026 | 16:00 |  | Sd may be availed subject to availability of 132kV Panyor-ziro-daprorijo-along link and 132kv Roing-Pasighat-Basar link
199 | OCC_243 | POWERGRID | 132KV-MELRIAT-ZUANGTUI-1 | D | Replacement of defective insulator string found during sample basis PID test.tower no. - LILO 8- 1 string, LILO 3-2 strings, TN 17- strings | 13/Nov/2026 | 07:30 | 13/Nov/2026 | 17:00 |  | PNOCC approved, shutdown may be availed subject to the availability of the 132 kV Aizawl–Melriat line, 132 kV Badarpur–Kolasib–Aizawl line, 132 kV Aizawl–Kumarghat line, 132 kV Jiribam–Tipaimukh–Aizawl link and 132 kV Aizawl–Lungmual line to ensure reliable power supply to the radially connected areas of the Mizoram Power System. Under the N-1 condition of the 132 kV Aizawl–Melriat line, the loading on the 132 kV Aizawl–Lungmual line shall be maintained within 50 MW to avoid the low-voltage conditions observed in the radially connected areas supplied from the Lungmual end of the Mizoram Power System. Consent from Mizoram is required.
200 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 13/Nov/2026 | 07:00 | 13/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
201 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 13/Nov/2026 | 07:00 | 13/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
202 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 13/Nov/2026 | 06:00 | 13/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
203 | OCC_243 | AEGCL | 132KV-TINSUKIA-LEDO-1 | D | CORRIDOR CLEANING LOC 30-35 | 13/Nov/2026 | 10:00 | 13/Nov/2026 | 16:00 | RE LEDO | SD may be availed subject to the availability of 132kV Tinsukia-Rupai -LEDO link.
204 | OCC_243 | AEGCL | 220KV-TINSUKIA-NTPS-1 | D | CORRIDOR CLEARANCE LOC 103 TO 136 | 13/Nov/2026 | 10:00 | 13/Nov/2026 | 17:00 | AGM TINSUKIA | S/D may be availed. 220 kV Tinsukia - Kathalguri D/C and 220 kV Tinsukia - NRPP- NTPS-Amguri-Mariani link to be kept in service.
205 | OCC_243 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 13/Nov/2026 | 08:00 | 13/Nov/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
206 | OCC_243 | POWERGRID | MISA - 220KV - BUS 1 | C | Testing of LBB and Busbar protection scheme under SCADA upgradation | 14/Nov/2026 | 09:00 | 15/Nov/2026 | 17:00 |  | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow. Consent from Assam is required | SD deferred as SD will be taking on daily basis and SD will be approved under PNOCC
207 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 14/Nov/2026 | 7:00 | 14/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
208 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 14/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
209 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-BASAR-1 | D | Vegetation Clearance | 14/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 |  | Sd may be availed subject to availability of 132kV Panyor-ziro-daprorijo-along link and 132kv Roing-Pasighat-Basar link
210 | OCC_243 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-1 | D | Jungle Clearance between Tower (6 to 8) | 14/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
211 | OCC_243 | MEPTCL | 220KV-MAWNGAP-BYRNIHAT (KILLING)-2 | D | Jungle Clearance between Tower (6 to 8) | 14/Nov/2026 | 08:00 | 14/Nov/2026 | 16:00 | Avail | SD may be availed subject to availability of 220/132kV ICTs at Killing S/s, 132 kV Killing- EPIP- Umtru- Umiam 3-Umiam 1-Mawngap-Mawlai-Umiam 1 link . Umiam1-Umiam-Nehu-Neighrims-Khleiriat(ME)-Kheliriat(PG) D/C link, Nehu-Mawlyndeep-Mustem Kheliriat , 132kV Panchgram - Lumshonong - Khleihriat link also needs to be present. The combined loading of 132kV Umiam1-Umiam and 132kV Umiam1-Mawlai line to be kept within 75MW
212 | OCC_243 | POWERGRID | 132KV-MELRIAT-ZUANGTUI-1 | D | Replacement of defective insulator string found during sample basis PID test.tower no. - LILO 8- 1 string, LILO 3-2 strings, TN 17- strings | 14/Nov/2026 | 07:30 | 14/Nov/2026 | 17:00 |  | PNOCC approved, shutdown may be availed subject to the availability of the 132 kV Aizawl–Melriat line, 132 kV Badarpur–Kolasib–Aizawl line, 132 kV Aizawl–Kumarghat line, 132 kV Jiribam–Tipaimukh–Aizawl link and 132 kV Aizawl–Lungmual line to ensure reliable power supply to the radially connected areas of the Mizoram Power System. Under the N-1 condition of the 132 kV Aizawl–Melriat line, the loading on the 132 kV Aizawl–Lungmual line shall be maintained within 50 MW to avoid the low-voltage conditions observed in the radially connected areas supplied from the Lungmual end of the Mizoram Power System. Consent from Mizoram is required.
213 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 14/Nov/2026 | 07:00 | 14/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | SD deferred due to SD of 132KV-ALONG-BASAR-1
214 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 14/Nov/2026 | 07:00 | 14/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
215 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 14/Nov/2026 | 06:00 | 14/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
216 | OCC_243 | AEGCL | NALKATA - 132KV - BUS 1 | D | AUGMENTATION OF BUS (MAIN BUS) | 14/Nov/2026 | 05:00 | 14/Nov/2026 | 17:00 | AGM NLP | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
217 | OCC_243 | POWERGRID | 132KV-DIMAPUR(PG)-IMPHAL-1 | C | Data Shutdown for Rectification of Lossy Span | 15/Nov/2026 | 10:30 | 17/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subject to the availability of Dimapur - Doyang and Dimapur-Misa
218 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 15/Nov/2026 | 7:00 | 15/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
219 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 15/Nov/2026 | 08:00 | 15/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
220 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-BASAR-1 | D | Vegetation Clearance | 15/Nov/2026 | 08:00 | 15/Nov/2026 | 16:00 |  | Sd may be availed subject to availability of 132kV Panyor-ziro-daprorijo-along link and 132kv Roing-Pasighat-Basar link
221 | OCC_243 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | D | Replacement of defective insulator string found during sample basis PID test.Tower no.- 18- 1 string, 16-2 strings, 14-1strings, 13-2 strings, 11-2strings | 15/Nov/2026 | 07:30 | 15/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Melriat - Simuii II
222 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 15/Nov/2026 | 07:00 | 15/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | SD deferred due to SD of 132KV-ALONG-BASAR-1
223 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 15/Nov/2026 | 07:00 | 15/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
224 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 15/Nov/2026 | 06:00 | 15/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
225 | OCC_243 | NEEPCO | KOPLII - UNIT 4 | C | APM | 15/Nov/2026 | 00:00 | 30/Nov/2026 | 23:59 | APM | SD may be availed. Consent of beneficiary is required.
226 | OCC_243 | AEGCL | NALKATA - 132KV - BUS 1 | D | AUGMENTATION OF BUS (MAIN BUS) | 15/Nov/2026 | 05:00 | 15/Nov/2026 | 17:00 | AGM NLP | SD may be availed. During the SD period, Dhemaji, Silapathar and Majuli area of Assam power Sytem will be under dark condition. Intimation to NERTS, MUML and NEEPCO
227 | OCC_243 | POWERGRID | FILTER BANK2 MAIN BAY AT BNC | D | bay AMP: CT tan delta, CB testing | 16/Nov/2026 | 09:00 | 16/Nov/2026 | 17:00 |  | S/D may be availed. NLDC consent is required.
228 | OCC_243 | POWERGRID | MISA - 220KV - BUS 2 | D | Testing of LBB and Busbar protection scheme under SCADA upgradation | 16/Nov/2026 | 8:00 | 16/Nov/2026 | 16:00 |  | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow. Consent from Assam is required
229 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-BALIPARA-2 L/R@ BALIPARA - 400KV | D | Reactor AMP work | 16/Nov/2026 | 09:00 | 16/Nov/2026 | 17:00 |  | SD may be subject to no outage of element
230 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 16/Nov/2026 | 7:00 | 16/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
231 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 16/Nov/2026 | 08:00 | 16/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
232 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 16/Nov/2026 | 08:00 | 16/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
233 | OCC_243 | Arunachal Pradesh | 132KV-ALONG-BASAR-1 | D | Vegetation Clearance | 16/Nov/2026 | 08:00 | 16/Nov/2026 | 16:00 |  | Sd may be availed subject to availability of 132kV Panyor-ziro-daprorijo-along link and 132kv Roing-Pasighat-Basar link
234 | OCC_243 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | D | Replacement of defective insulator string found during sample basis PID test.Tower no.- 18- 1 string, 16-2 strings, 14-1strings, 13-2 strings, 11-2strings | 16/Nov/2026 | 07:30 | 16/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Melriat - Simuii II
235 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 16/Nov/2026 | 07:00 | 16/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode | SD deferred due to SD of 132KV-ALONG-BASAR-1
236 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 16/Nov/2026 | 07:00 | 16/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
237 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 16/Nov/2026 | 06:00 | 16/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
238 | OCC_243 | NEEPCO | AGBPP - GTG 5 | C | Replacement of 415 V ACB's and retrofitting with new L&T make breaker at MCC panel | 16/Nov/2026 | 00:00 | 22/Nov/2026 | 23:59 | CSD | Sd may be availed. Consent from beneificiary is required.
239 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 150 TO 198 | 16/Nov/2026 | 08:00 | 16/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
240 | OCC_243 | AEGCL | MISA - 220KV - BUS 1 | C | 207/206-89A lsolator, BPl, Aluminium bus, Bus dropping, Alignment, testing & lnstallation, commissioning and erection of 220kV Post Insulator at 400/220kV Misa work | 17/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 | AGM SMG | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow.
241 | OCC_243 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 528 TO 194 | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
242 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-1 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 17/Nov/2026 | 09:30 | 17/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 132 kV Kameng-Khupi-Tenga-Balipara link and 400KV-BALIPARA-KAMENG-2. Intimation to Kameng
243 | OCC_243 | TSECL | 132KV-KUMARGHAT-P K BARI-1 | D | Routine Maintenance Work | 17/Nov/2026 | 09:00 | 17/Nov/2026 | 16:00 |  | SD may be availed, 132kV RC Nagar-Kumarghat & 132kV Badarpur-Karimganj-Kumarghat to be in service.
244 | OCC_243 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 L/R@ MISA - 400KV | C | Overhauling works (Line may be charged after SD of LR). During switching operation line will be out. | 17/Nov/2026 | 09:00 | 30/Nov/2026 | 17:00 |  | SD may be availed
245 | OCC_243 | POWERGRID | 220KV-MISA-KOPILI-2 | C | SAS upgradation (1. Existing cable dismantle and new cable termination, Shifting of PLCC panel, DC/AC termination from DCDB(48 & 220 V)/ACDB, M1 and M2 protection test (Day1-Day 9) with main bay. From 10-11th day, BusA sd will be proposed for testing of LBB /Busbar and protection Transfer scheme check | 17/Nov/2026 | 09:00 | 28/Nov/2026 | 17:00 |  | SD may be availed subjected to availability of 220KV-MISA-KOPILI-1 and 220KV-MISA-KOPILI-3. Intimation to NEEPCO
246 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 17/Nov/2026 | 7:00 | 17/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
247 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
248 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
249 | OCC_243 | POWERGRID | 132KV-MELRIAT-SINHMUI-1 | D | Replacement of defective insulator string found during sample basis PID test.Tower no.- 18- 1 string, 16-2 strings, 14-1strings, 13-2 strings, 11-2strings | 17/Nov/2026 | 07:30 | 17/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 132kV Melriat - Simuii II
250 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 17/Nov/2026 | 07:00 | 17/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
251 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 17/Nov/2026 | 07:00 | 17/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
252 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 17/Nov/2026 | 06:00 | 17/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
253 | OCC_243 | AEGCL | 220KV/132KV TINSUKIA-ICT-2 | D | ROUTINE BAY TESTING | 17/Nov/2026 | 09:00 | 17/Nov/2026 | 17:00 | AGM TSK | SD may be availed subjec to availability of 220kV NTPS-Bordubi-Tinsukia link, 132kV Behiating-Dibrugarh-Tinsukia link, 132kV Tinsukia-Rupai-Chapakhowa-Roing link, 132kV Tinsukia-Ledo-Rupai link, Considering N-1 contigency of 220/132kV ICT-1 at Tinsukia combined loading of Tinsukia ICT-1 and 132kV NTPS-Bordubi line should be maintained below 100 MW, line loading of 132kV NTPS-Bordubi line to be maintained below 50 MW.
254 | OCC_243 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 17/Nov/2026 | 09:00 | 17/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
255 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 150 TO 198 | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
256 | OCC_243 | AEGCL | 220KV-BTPS-RANGIA GSS-1 | D | PREVENTIVE MAINTENANCE | 17/Nov/2026 | 08:00 | 17/Nov/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-II and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
257 | OCC_243 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 104 to 102 | 18/Nov/2026 | 10:00 | 18/Nov/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
258 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-1 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 18/Nov/2026 | 09:30 | 18/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 132 kV Kameng-Khupi-Tenga-Balipara link and 400KV-BALIPARA-KAMENG-2. Intimation to POWERGRID
259 | OCC_243 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-1 | D | Routine Maintenance Work | 18/Nov/2026 | 09:00 | 18/Nov/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 2, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
260 | OCC_243 | POWERGRID | TIE BAY () OF 400KV-IMPHAL(PG)-400 KV NEW KOHIMA-2 AND IMPHAL(PG) - 400KV B/R 2 @IMPHAL(PG) - 400KV | D | AMP work of tie CB & tie CT | 18/Nov/2026 | 09:00 | 18/Nov/2026 | 14:00 |  | SD may be availed elements to remain in service via their respective main bays.
261 | OCC_243 | POWERGRID | MAIN BAY (W14Q1) OF HVDC 800KV BISWANATH CHARIALI POLE 1 @BISWANATH CHARIALI - 800KV | D | bay AMP: CT tan delta, CB testing | 18/Nov/2026 | 09:00 | 18/Nov/2026 | 18:00 |  | SD may be availed subject to availability of Pole-1 via Tie bay.
262 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 18/Nov/2026 | 7:00 | 18/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
263 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
264 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
265 | OCC_243 | MEPTCL | 132KV-AGIA-NANGALBIBRA-1 | D | Jungle clearance at T/Loc 155-158 | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 15:00 | Avail | S/D may be availed Subject to the availability of 132kV Agia-Mendipathar-Nangalbibra, 132kv Mawngap-Nongstoin-Nagalbibra link. Intimation to Assam
266 | OCC_243 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Jungle Clearance and checking the hardware at Tower NO (289 -292)) | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
267 | OCC_243 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Jungle Clearance and checking the hardware at Tower NO (289 -292)) | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
268 | OCC_243 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.292, 293,294,287 | 18/Nov/2026 | 07:30 | 18/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 132 kV Aizawal-Kolasib line
269 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 18/Nov/2026 | 07:00 | 18/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
270 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 18/Nov/2026 | 07:00 | 18/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
271 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 18/Nov/2026 | 06:00 | 18/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
272 | OCC_243 | NEEPCO | AGBPP - STG 2 | C | CONDENSER CLEANING AND RLA OF BOILERS | 18/Nov/2026 | 00:00 | 29/Nov/2026 | 00:00 |  | SD may be availed. Consent from Beneficiaries | SD deferred as NEEPCO won't be availing the SD
273 | OCC_243 | AEGCL | 132KV-HAILAKANDI-DULLAVCHERRA-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 18/Nov/2026 | 09:00 | 18/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to availabilty of 132kV PK Bari - Dharmanagar-Dullavcherra link. Intimation to Tripura
274 | OCC_243 | AEGCL | 220KV-JAWAHARNAGAR-SAMAGURI-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 237 TO 162 | 18/Nov/2026 | 08:00 | 18/Nov/2026 | 16:00 | AGM SSJI | SD may be availed subject to availability of 220kV Samaguri-Sonapur-Sarusajai link, 220kV Jawaharnagar-Sarusajai line.
275 | OCC_243 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 528 TO 194 | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
276 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | C | Data Shutdown for Rectification of Lossy Span | 19/Nov/2026 | 10:30 | 21/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subject to the availability of the Melriat - Aizawl
277 | OCC_243 | POWERGRID | 132KV-SILCHAR-MELRIAT-1 | C | Data Shutdown for Rectification of Lossy Span | 19/Nov/2026 | 10:30 | 20/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | SD deferred
278 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-1 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 19/Nov/2026 | 09:30 | 19/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 132 kV Kameng-Khupi-Tenga-Balipara link and 400KV-BALIPARA-KAMENG-2. Intimation to Kameng
279 | OCC_243 | POWERGRID | TIE BAY () OF 400KV-BISWANATH CHARIALI-BALIPARA-2 AND 400KV-BALIPARA-MISA-2 @BALIPARA - 400KV | D | Bay Equipment AMP | 19/Nov/2026 | 09:00 | 19/Nov/2026 | 17:00
280 | OCC_243 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Dismantling of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer (SST-2) SSB-C. | 19/Nov/2026 | 09:00 | 19/Nov/2026 | 15:00 | Day time shutdown of 7.5 MVA 132/33 kV Station Service Transformer-2 (SST-2) | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor. Consent from AP | SD deferred as NEEPCO won't be availing the SD
281 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 19/Nov/2026 | 7:00 | 19/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
282 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 19/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
283 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 19/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
284 | OCC_243 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-1 | D | Jungle Clearance and checking the hardware at Tower NO (289 -292)) | 19/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
285 | OCC_243 | MEPTCL | 220KV-BYRNIHAT (KILLING)-MISA-2 | D | Jungle Clearance and checking the hardware at Tower NO (289 -292)) | 19/Nov/2026 | 08:00 | 19/Nov/2026 | 16:00 | Avail | Sd may be availed subject to the availability of 400/220 KV ICT 1 and 2 at Killing.Intimation to NERTS
286 | OCC_243 | AEGCL | MISA - 220KV - BUS 2 | C | 207/206-89A lsolator, BPl, Aluminium bus, Bus dropping, Alignment, testing & lnstallation, commissioning and erection of 220kV Post Insulator at 400/220kV Misa work | 20/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 | AGM SMG | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow.
287 | OCC_243 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. No.292, 293,294,287 | 19/Nov/2026 | 07:30 | 19/Nov/2026 | 17:00 |  | SD may be availed subject to availability of 132 kV Aizawal-Kolasib line
288 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 19/Nov/2026 | 07:00 | 19/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
289 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 19/Nov/2026 | 07:00 | 19/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
290 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 19/Nov/2026 | 06:00 | 19/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
291 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-1 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 20/Nov/2026 | 09:30 | 20/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 132 kV Kameng-Khupi-Tenga-Balipara link and 400KV-BALIPARA-KAMENG-2. Intimation to POWERGRID
292 | OCC_243 | TSECL | 132KV-SURAJMANINAGAR (INDIGRID)-BUDHJANGNAGAR-1 | D | Routine Maintenance Work | 06/Nov/2026 | 09:00 | 06/Nov/2026 | 16:00 |  | SD may availed subject to availability of 132kV PK Bari(ISTS)-PK bari, 132kV Surajmaninagar(ISTS)-Surajmaninagar, 132 Palatana-Surajmaninagar link and 132kV PK Bari-Manu-Ambassa-Gamaitilla-Baramura-Jirania link. Combined loading of 132 PK Bari-Pk Bari and 132kV SM Nagar(TE)-SM Nagar(ISTS) needs to be maintained below 240MW during SD period. Intimation to INDIGRID
293 | OCC_243 | POWERGRID | MAIN BAY () OF IMPHAL(PG) - 400KV B/R 2 @IMPHAL(PG) - 400KV | D | AMP work on Main CB & Main CT | 20/Nov/2026 | 09:00 | 20/Nov/2026 | 14:00 |  | SD may be availed subject to availability of B/R 2 at Imphal(PG) via Tie Bay.
294 | OCC_243 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Dismantling of Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer (SST-2) SSB-C | 20/Nov/2026 | 09:00 | 20/Nov/2026 | 15:00 | Day time shutdown of 7.5 MVA 132/33 kV Station Service Transformer-2 (SST-2) | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor. Consent from AP | SD deferred as NEEPCO won't be availing the SD
295 | OCC_243 | POWERGRID | TIE BAY (W14Q2) OF HVDC 800KV BISWANATH CHARIALI POLE 1 AND FUTURE @BISWANATH CHARIALI - 800KV | D | bay AMP: CT tan delta, CB testing | 20/Nov/2026 | 09:00 | 20/Nov/2026 | 18:00 |  | SD may be availed subject to availability of Pole-1 via Main bay.
296 | OCC_243 | POWERGRID | 132KV-HAFLONG-UMRANSHU-1 | D | TLA installation in the whole line. | 20/Nov/2026 | 7:00 | 20/Nov/2026 | 16:00 |  | SD may be availed subject the availability of 132kV Khandong - Umrangshu and 132kV Jiribam - Halflong
297 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
298 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
299 | OCC_243 | AEGCL | 132KV-SRIKONA-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 20/Nov/2026 | 09:00 | 20/Nov/2026 | 16:00 | AGM PNG | SD may be availed
300 | OCC_243 | AEGCL | 220KV-AZARA-BOKO-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 284 TO 209 | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 | AGM SSJI | S/D may be availed. 220 kV Agia - Boko line and 220 kV Agia - Chaygaon-Mirza line to be kept in service
301 | OCC_243 | AEGCL | 220KV-AGBPP-TINSUKIA-1 | D | ROUTINE TESTING OF BAY EQUIPMENTS & CORRIDOR CLEARANCE LOC 31 TO 52 | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 | AGM TINSUKIA | S/D may be availed subject to the availability of 220 kV Tinsukia-Kathalguri II, 220 kV Tinsukia - NTPS and 220 kV Tinsukia - NRPP - NTPS line, Intimation to NEEPCO
302 | OCC_243 | AEGCL | 220KV-NTPS-AMGURI-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING LOC 528 TO 194 | 22/Nov/2026 | 08:00 | 22/Nov/2026 | 16:00 | AGM MARIANI | S/D may be availed subject to availability of 220 k Mariani-Amguri line.
303 | OCC_243 | AEGCL | 220KV-BTPS-RANGIA GSS-2 | D | PREVENTIVE MAINTENANCE | 20/Nov/2026 | 08:00 | 20/Nov/2026 | 16:00 | AGM RANGIA | S/D may be availed subject to availability of 220kV BTPS - Rangia ckt-I and 132kV Rangia - Motanga. SPS related to tripping of 220kV BTPS - Rangia D/C to be kept in ON condition.
304 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 20/Nov/2026 | 07:00 | 20/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
305 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 20/Nov/2026 | 07:00 | 20/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
306 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 20/Nov/2026 | 06:00 | 20/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
307 | OCC_243 | POWERGRID | 220KV-MISA-DIMAPUR (PG)-1 | C | Data Shutdown for Rectification of Lossy Span | 21/Nov/2026 | 10:30 | 21/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subject to the availability of Dimapur - Doyang, Dimapur-Imphal, Misa - Kopili and Misa - Balipara
308 | OCC_243 | Arunachal Pradesh | 132KV-KAMENG-KHUPI-1 | C | Reconductoring of Kimi-Khuppi line | 21/Nov/2026 | 08:00 | 25/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kv Balipara-Tenga-Khupi link. Intimation to NEEPCO and NERTS, FTC procedure to followed before charging of the line once the complete line reconducturing work . Inimation to NEEPCO
309 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
310 | OCC_243 | POWERGRID | 132KV-TEZU-NAMSAI-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 13Nos located at interior hilly stretches requiring significant Head-loading, Vegetation clearance in critical spans Insulator replacement in 132kV Tezu Namsai TL :- 11(02), 16(01), 37(01), 48(02), 53(04), 57(02), 69(01), 73(01). | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 220kV Namsai-Kathalguri link, 132kV Ranganadi-Ziro-Daporjio-Basar-Along-Roing link, Tinsukia-Rupai-chapakhowa-roing link. Consent from AP is required.
311 | OCC_243 | MEPTCL | 132KV-KAHILIPARA-UMTRU-1 | D | Jungle Clearance Hardware fitting at Tower (3 &4) will be checked | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
312 | OCC_243 | MEPTCL | 132KV-KAHILIPARA-UMTRU-2 | D | Jungle Clearance Hardware fitting at Tower (3 &4) will be checked | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 16:00 | Avail | SD may be availed, intimation to SLDC Assam
313 | OCC_243 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement found during PID at Loc. 23,24,26,68,69. | 21/Nov/2026 | 08:00 | 21/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. Combined loading of AP capital and Gohpur exceeds 180 MW. Consent from Assam and AP is required
314 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 21/Nov/2026 | 07:00 | 21/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
315 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 21/Nov/2026 | 07:00 | 21/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
316 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 21/Nov/2026 | 06:00 | 21/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
317 | OCC_243 | AEGCL | 132KV-TINSUKIA-RUPAI-1 | D | CORRIDOR CLEANING LOC 1 TO 108 | 21/Nov/2026 | 09:30 | 21/Nov/2026 | 16:00 | RE RUPAI | SD may be availed Subject to availability of Kathalguri-Namsai - Tezu -Roing -Chapakhowa -Rupai link & 132 Rupai -Margarita -Tinsukia link
318 | OCC_243 | AEGCL | 132KV-SRIKONA-PANCHGRAM (NEW)-1 | D | PREVENTIVE MAINTENANCE & CORRIDOR CLEANING | 21/Nov/2026 | 09:00 | 21/Nov/2026 | 16:00 | AGM PNG | SD may be availed
319 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 21/Nov/2026 | 06:00 | 21/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
320 | OCC_243 | POWERGRID | 400KV-MISA-MARIANI (PG)-1 | C | Data Shutdown for Rectification of Lossy Span | 22/Nov/2026 | 10:30 | 24/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subject to the availability of Mariani - Mokokchung
321 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 22/Nov/2026 | 08:00 | 22/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
322 | OCC_243 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement found during PID at Loc. 23,24,26,68,69. | 22/Nov/2026 | 08:00 | 22/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. Combined loading of AP capital and Gohpur exceeds 180 MW. Consent from Assam and AP is required
323 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 22/Nov/2026 | 07:00 | 22/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
324 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 22/Nov/2026 | 07:00 | 22/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
325 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 22/Nov/2026 | 06:00 | 22/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
326 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 22/Nov/2026 | 06:00 | 22/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
327 | OCC_243 | POWERGRID | 132KV-BADARPUR-KOLASIB-1 | C | Data Shutdown for Rectification of Lossy Span | 23/Nov/2026 | 10:30 | 25/Nov/2026 | 18:30 | Data Shutdown for Rectification of Lossy Span | Subjec to the availbility of the badarpur - Khelieriat and Kolasib Aizawl
328 | OCC_243 | TSECL | 132KV-P K BARI-PK BARI (INDIGRID)-1 | D | Routine Maintenance Work | 07/Nov/2026 | 09:00 | 07/Nov/2026 | 16:00 |  | SD may be availed subject to the availability of 132kV Suramaningar-Surajmaninagar(ISTS), 132kV Surajmaninagar(ISTS)-Budhjungnagar and 132kV PKbari-Manu-Ambassa-Gamaitila-Barmura-Jiranaia-Budhjungnagar link. Combined loading of 132kV SM Nagar(ISTS) - SM Nagar and 132kV SM Nagar(ISTS) - Budhjungnagar to maintained below 180 MW during the shutdown period. Intimation to Indigrid
329 | OCC_243 | POWERGRID | 132KV-LEKHI-RANGANADI-1 | D | Critical Insulator Replacement found during PID at Loc. 23,24,26,68,69. | 23/Nov/2026 | 08:00 | 23/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400/132kV ICT I & II at Panyor, 132kV Panyor – Ziro-Along-Daporijo-Pasighat – Roing link, 132kV Panyor – Pare and 132kV Panyor – Itanagar. No generation of Panyor can be scheduled. Combined loading of AP capital and Gohpur exceeds 180 MW. Consent from Assam and AP is required
330 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 23/Nov/2026 | 08:00 | 23/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
331 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 23/Nov/2026 | 08:00 | 23/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
332 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 23/Nov/2026 | 07:00 | 23/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
333 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 23/Nov/2026 | 07:00 | 23/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
334 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 23/Nov/2026 | 06:00 | 23/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
335 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 23/Nov/2026 | 06:00 | 23/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
336 | OCC_243 | NETCL | 400KV-AZARA-BONGAIGAON-1 | D | Replacement of rusted jumper cone N&B, Tightening of loose jumper cone, CC Ring N&B, fixing of dislocated VD etc | 24/Nov/2026 | 10:00 | 24/Nov/2026 | 14:00 |  | S/D may be availed subject to availabilty of 400 kV Bongaigaon-Killing, 400 kV Azara-Silchar, 220 kV Salakati-BTPS-Agia-Azara link and 220 kV Balipara-Sonabil D/C. NER ATC/TTC to be revised. The Dia must be completed after swithing of elements for reliable system operation.400kV Azara line shares the dia with Balipara-III at Bongaigaon.
337 | OCC_243 | POWERGRID | 220KV-BONGAIGAON-SALAKATI-1 | D | AMP OF BAY EQUIPMENTS. | 24/Nov/2026 | 09:30 | 24/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 220KV-BONGAIGAON-SALAKATI-2, 220kV Bongaigaon-BTPS D/C(ICT)
338 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 24/Nov/2026 | 09:30 | 24/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 400kV Balipara - Kameng 1
339 | OCC_243 | POWERGRID | MAIN BAY (429) OF HVDC 800KV BISWANATH CHARIALI POLE 2 @BISWANATH CHARIALI - 800KV | D | bay AMP: CT tan delta, CB testing | 24/Nov/2026 | 09:00 | 24/Nov/2026 | 18:00 |  | SD may be availed subject to no outage of elements. Tie bay must be in service
340 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 24/Nov/2026 | 08:00 | 24/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
341 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 24/Nov/2026 | 08:00 | 24/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
342 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68 | 24/Nov/2026 | 08:00 | 24/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
343 | OCC_243 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-1 | D | AMP OF ICT, RELAY TESTING, OIL TOP-UP | 24/Nov/2026 | 08:00 | 24/Nov/2026 | 19:00 |  | SD may be availed subject to the availability of ICT II and III at Mokokching. Combined loaidng in ICT-II and ICT-III of Mokokchung to maintained below 40 MW.
344 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 24/Nov/2026 | 07:00 | 24/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
345 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 24/Nov/2026 | 07:00 | 24/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
346 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 24/Nov/2026 | 06:00 | 24/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
347 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 24/Nov/2026 | 06:00 | 24/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
348 | OCC_243 | MEPTCL | 220KV-NEW SHILLONG-MAWNGAP-2 | D | Tightening of nuts and bolts between Tower Location 101 to 99 | 25/Nov/2026 | 10:00 | 25/Nov/2026 | 15:00 | Avail | SD may be availed subject to availability of 220KV-NEW SHILLONG-MAWNGAP-1
349 | OCC_243 | Arunachal Pradesh | 132KV-DAPORIJU-ZIRO-1 | D | Vegetation Clearance | 25/Nov/2026 | 09:30 | 25/Nov/2026 | 16:00 |  | SD may be availed subject to availability of 132kV Panyor - Ziro, 132kV Daporijo-Basar-Along-Pasighat-Roing link, 132kV Roing-Chapakhowa - Rupai I Tinsukia link and Roing-Tezu-Namsai-Kathalguri link. Intimation to NERTS | SD deferred due to SD of 400kV Balipara-Panyor line and 132kV oing tezu
350 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 25/Nov/2026 | 09:30 | 25/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 400kV Balipara - Kameng 1
351 | OCC_243 | POWERGRID | MAIN BAY (413) OF 400KV-NEW KOHIMA-MARIANI (PG)-2 @MARIANI (PG) - 400KV | D | AMP of bay equipment | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
352 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
353 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
354 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68 | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
355 | OCC_243 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-1 | D | AMP OF ICT, RELAY TESTING, OIL TOP-UP | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 19:00 |  | SD may be availed subject to the availability of ICT II and III at Mokokching. Combined loaidng in ICT-II and ICT-III of Mokokchung to maintained below 40 MW.
356 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 25/Nov/2026 | 07:00 | 25/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
357 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 25/Nov/2026 | 07:00 | 25/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
358 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 25/Nov/2026 | 06:00 | 25/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
359 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 25/Nov/2026 | 06:00 | 25/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
360 | OCC_243 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | CORRIDOR CLEANING | 25/Nov/2026 | 09:00 | 25/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
361 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-1 | D | LINE MAINTENANCE LOC 199 TO 249 | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 2 & 132 kV Pare North Lakimpur & Nirjuli - North Lakimpur line..
362 | OCC_243 | AEGCL | 220KV-SAMAGURI-SONAPUR-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 237 TO 162 | 25/Nov/2026 | 08:00 | 25/Nov/2026 | 16:00 | AGM SMG | S/D may be availed subject to availability of 220 kV Sarusajai-Jawaharnagar-Samaguri link, 220 kV Sarusajai - Sonapur line and 220 kV Sarusajai-Azara DC.
363 | OCC_243 | POWERGRID | SALAKATI - 220KV - BUS 2 | D | For attending hotspot in Bus Isolators. | 26/Nov/2026 | 09:30 | 26/Nov/2026 | 17:00 |  | SD may be availed subject to no outage of elements, considering N-1 contigency of other bus combined loading of 220kV Salakati-BTPS D/C and 400/220 kV ICTs at Bgtpp to be kept within 600 MW.
364 | OCC_243 | POWERGRID | 220KV-BONGAIGAON-SALAKATI-2 | D | AMP OF BAY EQUIPMENTS. | 26/Nov/2026 | 09:30 | 26/Nov/2026 | 17:00 |  | 220KV Salakati-Bongaigaon CKT-1 and 220kV Salakati-Alipurduar D/C needs to be present.
365 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 26/Nov/2026 | 09:30 | 26/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 400kV Balipara - Kameng 1
366 | OCC_243 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Installation of new aluminium Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer (SST-2) SSB-C. | 26/Nov/2026 | 09:00 | 26/Nov/2026 | 15:00 | Day time shutdown of 7.5 MVA 132/33 kV Station Service Transformer-2 (SST-2) | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor. Consent from AP | SD deferred as NEEPCO won't be availing the SD
367 | OCC_243 | POWERGRID | TIE BAY (429) OF HVDC 800KV BISWANATH CHARIALI POLE 2 AND FUTURE @BISWANATH CHARIALI - 800KV | D | bay AMP: CT tan delta, CB testing | 26/Nov/2026 | 09:00 | 26/Nov/2026 | 18:00 |  | SD may be availed subject to no outage of elements.
368 | OCC_243 | POWERGRID | MISA - 220KV - BUS 1 | C | Testing of LBB and Busbar protection scheme under SCADA upgradation | 26/Nov/2026 | 09:00 | 27/Nov/2026 | 17:00 |  | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow. Consent from Assam is required | SD deferred as SD will be taking on daily basis and SD will be approved under PNOCC
369 | OCC_243 | INDIGRID | 400KV-BONGAIGAON-ALIPURDUAR-1 | D | AMP work in the line | 25/Nov/2026 | 09:00 | 25/Nov/2026 | 15:00 |  | SD may be availed subject to the availabitiy of 400kV Bongaigaon - Alipurduar 2 and 400kV Bongaigaon - New Siliguri D/C. Intimation to NERTS. Consent from NLDC is required
370 | OCC_243 | TSECL | 132KV-AGARTALA (79 TILLA)-ROKHIA-2 | D | Routine Maintenance Work | 26/Nov/2026 | 09:00 | 26/Nov/2026 | 16:00 |  | S/D may be availed subject to availability of 132kV Agartala-Rokhia 1, 132kV Monarchak-Rokhia, 132kV Palatana - Udaipur - Monarchak link and 132kV Monarchak - Rabindranagar-Belonia-Bokafa - Udaipur link.
371 | OCC_243 | POWERGRID | TIE BAY (414) OF 400KV-NEW KOHIMA-MARIANI (PG)-2 AND FUTURE @MARIANI (PG) - 400KV | D | AMP of bay equipment | 26/Nov/2026 | 08:00 | 26/Nov/2026 | 16:00 |  | SD may be availed subject to no outage of elements.
372 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 26/Nov/2026 | 08:00 | 26/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
373 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 26/Nov/2026 | 08:00 | 26/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
374 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-1 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68 | 26/Nov/2026 | 08:00 | 26/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-2, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
375 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 26/Nov/2026 | 07:00 | 26/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
376 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 26/Nov/2026 | 07:00 | 26/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
377 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 26/Nov/2026 | 06:00 | 26/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
378 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 26/Nov/2026 | 06:00 | 26/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
379 | OCC_243 | AEGCL | 220KV-TINSUKIA-NRPP-1 | D | CORRIDOR CLEARANCE LOC 51 TO 80 | 26/Nov/2026 | 10:00 | 26/Nov/2026 | 17:00 | AGM TINSUKIA | S/D may be availed Subject to the availability of 132kV Tinsukia-NTPS and 132kV NTPS-NRPP
380 | OCC_243 | AEGCL | 132KV-DHARMANAGAR (MISSION TILLA)-DULLAVCHERRA-1 | D | CORRIDOR CLEANING | 26/Nov/2026 | 09:00 | 26/Nov/2026 | 16:00 | AGM PNG | SD may be availed subject to the availability of 132kV PK bari-dharmanagar link and 132 Hailakandi-Dullavcherra link. Consent from Tripura
381 | OCC_243 | AEGCL | 220KV-CHAYGAON GSS-AGIA-1 | D | CORRIDOR CLEANING & PREVENTIVE MAINTENANCE LOC 209 TO 235 | 26/Nov/2026 | 08:30 | 26/Nov/2026 | 16:30 | AGM SSJI | SD may be availed subject to availability of 220 kV Agia - Boko - Mirza, 400kV Bongaigaon - Azara, 400/220kV ICTs at Azara S/S and 132kV Mirza-Chaygaon line.
382 | OCC_243 | AEGCL | 132KV-GOHPUR-NALKATA-2 | D | LINE MAINTENANCE LOC 199 TO 249 | 26/Nov/2026 | 08:00 | 26/Nov/2026 | 15:00 | AGM NLP | S/D may be availed subject to availability of 132 kV Gohpur - Nalkata ckt 1 & 132 kV Pare N Lakimpur & Nirjuli - North Lakimpur line..
383 | OCC_243 | NETCL | 400KV-BONGAIGAON-BYRNIHAT (KILLING) | D | Replacement of damaged insulators and rusted jumper cone N&B, Tightening of loose jumper cone, CC Ring N&B etc | 30/Nov/2026 | 10:00 | 30/Nov/2026 | 14:00 |  | S/D may be availed subject to availability of 400 kV Bongaigaon – Azara, 400 kV Silchar – Killing, 400 kV Silchar – Azara, 220 kV Agia – BTPS D/C, 220 kV Balipara – Sonabil – Samaguri D/C. The combined loading of the 220 kV BTPS–Agia D/C line should be maintained below 240 MW during the shutdown period to ensure safe and reliable operation. ATC/TTC needs to be revised.
384 | OCC_243 | POWERGRID | 400KV-BALIPARA-KAMENG-2 | D | For Phase -V defect rectification works. This shutdown involves defect rectification works in both the circuits, such as CC ring replacement & nut bolts tightening, VD Displaced rectification, cotter pins fixing, tightening of loose jumper nut bolts, proper alignment of arcing horns and bird guard fixing. The locations are as follows: 2,3,6,10,11,12,21,30,36,37,38,39,42,49,62,67,68,78,79,80,81,82,83,84,86,99,101,115,119,120,123,126,134,141,148 | 27/Nov/2026 | 09:30 | 27/Nov/2026 | 16:30 |  | SD may be availed subject to availability of 400kV Balipara - Kameng 1
385 | OCC_243 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Installation of new aluminium Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer (SST-2) SSB-C. | 27/Nov/2026 | 09:00 | 27/Nov/2026 | 15:00 | Day time shutdown of 7.5 MVA 132/33 kV Station Service Transformer-2 (SST-2) | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor. Consent from AP | SD deferred as NEEPCO won't be availing the SD
386 | OCC_243 | INDIGRID | 400KV-BONGAIGAON-ALIPURDUAR-2 | D | AMP work in the line | 27/Nov/2026 | 09:00 | 27/Nov/2026 | 15:00 |  | SD may be availed subject to the availabitiy of 400kV Bongaigaon - Alipurduar 1 and 400kV Bongaigaon - New Siliguri D/C.Intimation to NERTS. Consent from NLDC is required
387 | OCC_243 | POWERGRID | MAIN BAY (412) OF MARIANI (PG) - 400KV B/R 2 AND @MARIANI (PG) - 400KV | D | AMP OF BAY EQUIPMENTS | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 16:00
388 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
389 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
390 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68,101,102 | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
391 | OCC_243 | POWERGRID | 400KV/132KV SILCHAR-ICT-1 | D | AMP & ATTENDING CC SIR POINT | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of ICT 2 and ICT 3.
392 | OCC_243 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-2 | D | AMP OF ICT, RELAY TESTING, OIL TOP-UP | 27/Nov/2026 | 08:00 | 27/Nov/2026 | 19:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-3 of Mokokchung to maintained below 40 MW.
393 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 27/Nov/2026 | 07:00 | 27/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
394 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 27/Nov/2026 | 07:00 | 27/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
395 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 27/Nov/2026 | 06:00 | 27/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
396 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 27/Nov/2026 | 06:00 | 27/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
397 | OCC_243 | NEEPCO | 132KV/33KV RANGANADI-ICT-2 | D | Installation of new aluminium Metal Bus Duct Enclosure of 2.5 MVA 33/0.415 kV S/S Transformer (SST-2) SSB-C. | 28/Nov/2026 | 09:00 | 28/Nov/2026 | 15:00 | Day time shutdown of 7.5 MVA 132/33 kV Station Service Transformer-2 (SST-2) | SD May be availed subject to availability of 132/33kV ICT-1 at Panyor. Consent from AP | SD deferred as NEEPCO won't be availing the SD
398 | OCC_243 | POWERGRID | MISA - 220KV - BUS 2 | D | Testing of LBB and Busbar protection scheme under SCADA upgradation | 28/Nov/2026 | 8:00 | 28/Nov/2026 | 16:00 |  | SD may be availed subject to availability of other 220 kV Misa Bus & 220kV Bailpara-Sonabil-Samaguri D/C link. All elements must be shifted to Bus before taking the SD. .Following elements needs to be in service: 220/132kV Kopili ICT-1 &2, 132kV Kopili-Khandong D/C, 132kV Khandong-Khleiriat D/C, 132kV Khleiriat-Kheliriat D/C, 132kV Badarpur-Khleiriat, 132kV Doyang-Dimapur link, 132kV Dimapur-Imphal & 132kV Dimapur-Kohima link. Samaguri gate flow to be maintained within 460 MW, Lower kopili generation and Langpi generation has 75% and 20-25% sensitivity respectivelyon Samaguri gate flow, Lower kopili generation can be scheduled to control Samaguri gate flow. Consent from Assam is required
399 | OCC_243 | Arunachal Pradesh | 132KV-BALIPARA-TENGA-1 | D | Earth cutting along line corridor at locations of low ground clearance and vegetation clearance | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV Kameng-Khupi-Tenga link. Intimation to NERTS
400 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
401 | OCC_243 | POWERGRID | 132KV-ROING-TEZU-1 | D | Shutdown for replacement of defective insulator (Sample PID) at 08Nos, Phase - V defect rectification at 15locations, Vegetation clearance in critical spans. Insulator replacement in 132kV Roing Tezu TL :- 111(01), 114(01), 126(01), 139(02), 169(02), 192(01). Phase - V Defect rectification in 132kV Roing Tezu TL : - 108,117,120,123-124,125-126,132,139-140,144,148,170,175-176,177,184,191,195,197-196,213,225,227,237,238,239,240,241,114,177,179,231,240. | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 16:00 |  | SD may be availed subject the availability of Ranganadi-Ziro-Daporijo-Basar-Along-Pasighat-Roing link, Tinsukia-Rupai-Chapakhowa-Roing link and Tezu-Namsai-Kathalguri link
402 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68,101,102 | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
403 | OCC_243 | POWERGRID | 220KV/132KV MOKOKCHUNG-ICT-2 | D | AMP OF ICT, RELAY TESTING, OIL TOP-UP | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 19:00 |  | SD may be availed subject to the availability of ICT I and II at Mokokching. Combined loaidng in ICT-1 and ICT-3 of Mokokchung to maintained below 40 MW.
404 | OCC_243 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement found during PID at Loc.82,102,124,126,127,129. | 28/Nov/2026 | 08:00 | 28/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. FTC required before final charging Intimation to Nerts.
405 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 28/Nov/2026 | 07:00 | 28/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
406 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 28/Nov/2026 | 07:00 | 28/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
407 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 28/Nov/2026 | 06:00 | 28/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
408 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 28/Nov/2026 | 06:00 | 28/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
409 | OCC_243 | POWERGRID | 400KV-SILCHAR-IMPHAL(PG)-1 | C | Data Shutdown for Rectification of Lossy Span | 29/Nov/2026 | 10:30 | 30/Nov/2026 | 18:30 |  | Subject to the availablity of Imphal - Dimapur and Imphal - New Kohima - mariani.
410 | OCC_243 | Arunachal Pradesh | 132KV-BALIPARA-TENGA-1 | D | Earth cutting along line corridor at locations of low ground clearance and vegetation clearance | 29/Nov/2026 | 08:00 | 29/Nov/2026 | 16:00 |  | Sd may be availed subject to the availability of 132kV Kameng-Khupi-Tenga link. Intimation to NERTS
411 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 29/Nov/2026 | 08:00 | 29/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
412 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68,101,102 | 29/Nov/2026 | 08:00 | 29/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
413 | OCC_243 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement found during PID at Loc.82,102,124,126,127,129. | 29/Nov/2026 | 08:00 | 29/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. FTC required before final charging Intimation to Nerts.
414 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 29/Nov/2026 | 07:00 | 29/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
415 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 29/Nov/2026 | 07:00 | 29/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
416 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 29/Nov/2026 | 06:00 | 29/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
417 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 29/Nov/2026 | 06:00 | 29/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD
418 | OCC_243 | NRTS | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-1 | D | For shutdown and isolation of HVDC Electrode line-1 | 29/Nov/2026 | 8:00 | 29/Nov/2026 | 12:00 |  | SD may be availed subject to availability of 400kV BNC-Balipara-Bongaingaon link, 400kV Bongaingaon-Azara line, 220kV Balipara-Sonabil D/C.
419 | OCC_243 | NRTS | 800 KV HVDC AGRA-BISHWANATH CHARIALI (PG) CKT-2 | D | For shutdown and isolation of HVDC Electrode line-1 | 29/Nov/2026 | 8:00 | 29/Nov/2026 | 12:00
420 | OCC_243 | POWERGRID | KUMARGHAT - 132KV - BUS 2 | D | Warranty test of bus compartments associated with bus 2 at Kumarghat SS | 30/Nov/2026 | 09:00 | 30/Nov/2026 | 16:00 |  | SD may be availed subject to availability of all elements via Kumarghat Bus-1
421 | OCC_243 | POWERGRID | 220KV-MISA-KOPILI-1 | D | SAS upgradation (1. Existing cable dismantle and new cable termination, Shifting of PLCC panel, DC/AC termination from DCDB(48 & 220 V)/ACDB, M1 and M2 protection test (Day1-Day 9) with main bay. From 10-11th day, BusA sd will be proposed for testing of LBB /Busbar and protection Transfer scheme che.Continious Shutdown required till 11.12.2026. | 30/Nov/2026 | 09:00 | 30/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 220kV Misa-Kopili Ckt 3 and 2
422 | OCC_243 | POWERGRID | AR of 132KV-TEZU-NAMSAI-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV TEZU-NAMSAI TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV TEZU-NAMSAI 2ND CIRCUIT UNDER NERES-XXIII. | 30/Nov/2026 | 08:00 | 30/Nov/2026 | 16:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
423 | OCC_243 | POWERGRID | 400KV-BISWANATH CHARIALI-RANGANADI-2 | D | For replacement of conventional porcelain insulators by composite long rod polymer insulators at Power/Deep valley/River/SH/NH crossing locations between Loc. 26,27,54,55,67,68,101,102 | 30/Nov/2026 | 08:00 | 30/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 400KV-BISWANATH CHARIALI-RANGANADI-1, 400/132kV ICT 1 & 2 at Panyor, 400/132kV ICT 1 & 2 at BNC(PG), 132kV Panyor-Lekhi-Nirjuli link, 132kV Panyor-Pare-Itanagar(Chimpu)-BNC(PG) link and 132kV Panyor-Ziro-Daporizo-Basar-Along Pasighat-Roing link. When one machine of Panyor is scheduled, one machine of Pare needs to be scheduled. When two machine of Panyor, two machine of Pare needs to be scheduled. Maximum 260 MW of Panyor can be scheduled during the SD period. Intimation to NEEPCO
424 | OCC_243 | POWERGRID | 132KV-GOHPUR-NIRJULI-1 | D | Critical Insulator Replacement found during PID at Loc.82,102,124,126,127,129. | 30/Nov/2026 | 08:00 | 30/Nov/2026 | 17:00 |  | SD may be availed subject to the availability of 132kV BNC(PG)-Gohpur-N Lakhimpur-Nirjuli link,132kV Panyor-Lekhi-Nirjuli link and 132kV Pare-Nirjuli link. FTC required before final charging Intimation to Nerts.
425 | OCC_243 | POWERGRID | AR of 132KV-PASIGHAT-ROING-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Pasighat-Roing TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Pasighat-Roing 2ND CIRCUIT UNDER NERES-XXIII. | 30/Nov/2026 | 07:00 | 30/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED | A/R may be kept in Non-auto mode
426 | OCC_243 | POWERGRID | AR of 132KV-ROING-TEZU-1 | D | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. AUTORECLOSURE IN 132KV Roing-TEZU TO BE SWITCHED OFF TO FACILITATE SAFE STRINGING WORKS OF 132KV Roing-TEZU 2ND CIRCUIT UNDER NERES-XXIII. | 30/Nov/2026 | 07:00 | 30/Nov/2026 | 17:00 | SHUTDOWN NOT REQUIRED ONLY AR NON-AUTO REQUIRED. | A/R may be kept in Non-auto mode
427 | OCC_243 | POWERGRID | 132KV-PALATANA-SURAJMANI NAGAR-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Daily Shutdown is required till 06.12.2026 | 30/Nov/2026 | 06:00 | 30/Nov/2026 | 20:00 |  | SD may be availed subject to availability of 132kV SM Nagar(ISTS) – SM Nagar, 132kV SM Nagar(ISTS) – Budhjungnagar- SM Nagar link and 132kV PK Bari(ISTS) – PK Bari. Combined Loading of 132kV SM Nagar(ISTS) – SM Nagar and 132kV SM Nagar(ISTS) – Budhjungnagar to be maintained below 180 MW. SPS related to tripping of 132kV Palatana – SM Nagar to be kept off before availing shutdown. Consent required from Tripura to maintain line loading during real time.
428 | OCC_243 | POWERGRID | 400KV-SURAJMANINAGAR (STERLITE)-PALATANA-1 | D | For erection of permanent tower in between Loc 91 & 92 in place of 03 nos ERS of Palatana-SM Nagar TL and associated stringing and shifting works. Shutdown is required till 21.12.2026 | 30/Nov/2026 | 06:00 | 30/Nov/2026 | 23:59 |  | SD may be availed subject to the availability of 400kV Palatana - Silchar D/C and 400kV Sichar- PK Bari - SM Nagar link. SPS related to tripping of 400kV Palatana - Sichar D/C to be kept in On during shutdown period. | Already applied under Continuous SD

## Sheet2
SD may be availed, elements should be segregated in following way Two 220kV Misa-Kopili line, One Misa-Samaguri line, One Misa-dimapur line, One 220kV Misa-Killing line and One 500 MVA 400/220kV Misa ICT in one bus. One 220kV Misa-Kopili line, One Misa-Samaguri line, One Misa-dimapur line, One 220kV Misa-killing line, One 500 MVA 400/220kV Misa and 315 MVA 400/220kV ICT in other bus.
SD may be availed, elements should be segregated in following way Bus 1: Two 220kV Misa-Kopili lines, One Misa-Samaguri line, One Misa-Dimapur line, One 220kV Misa-Killing line, and One 500 MVA 400/220kV Misa ICT. Bus 2: One 220kV Misa-Kopili line, One Misa-Samaguri line, One Misa-Dimapur line, One 220kV Misa-Killing line, One 500 MVA 400/220kV Misa ICT, and One 315 MVA 400/220kV ICT.